## TestRaporu
| OTOMASYON TEST RAPORU AUTOMATION TEST REPORT |  |  |  | Doküman No Document Number | Form-550
[5 empty] | Yayın Tarihi Publication Date | 2025-10-10
[5 empty] | Rev. No/Tarih Rev. No/Date | 00/00.00.0000
[5 empty] | Güncelleme Tarihi Update Date | 2025-10-10
[5 empty] | Sayfa No Page Number | 1/2
PROJE / PROJECT |  |  |  | Tarih/Date
Sipariş No Order No
Proje Adı Project Name
AHU Adı AHU Name
FANLAR / FANS
Fan Tipi Fan Type |  |  | Üfleme Fan Sayısı Supply Fan Number
Debi Kontrol Air Flow Control |  |  | Dönüş Fan Sayısı Return Fan Number
Basınç Kontrol Pressure Control |  |  | Üfleme Debi %25 Supply Air Flow (%25)
Dönüş Debi %25 Return Air Flow (%25)
MODÜLLER / MODULES
Rotor Heat Recovery Wheel |  |  | Soğutma Vanası 2 Cooling Valve 2 (Jet Cooling)
Çevrimsel Batarya RunAround Batary |  |  | Isıtma Vanası 2 Heating Val2(Dehumidification)
ChangeOver Vana ChangeOver Valve |  |  | Faz Koruma Rölesi Phase Protection Relay
Elektrikli Isıtıcı Electrical Heater |  |  | Bakım Anahtarı Maintenance Switch
DX Batarya DX Coil |  |  | Fan Kapı Anahtarı Fan Door Switch
DX Kademe Sayısı DX Stage Number |  |  | Yangın Alarm Fire Alarm
Nemlendirici Humidifier |  |  | Acil Durum Butonu Emergency
Nem. Kademe Sayısı Hum. Stage Number |  |  | Donma Termostatı Frost Thermostat
Isıtma Vanası Heating Valve 1 |  |  | Yüksek Sıcaklık Termostatı High Temp. Thermostat
Soğutma Vanası 1 Cooling Valve 1
DAMPERLER / DAMPERS
Taze Hava Damperi |  |  | Egzos Damperi
Fresh Air Damper |  |  | Exhaust Damper
Üfleme Damperi |  |  | Karışım Damperi
Supply Damper |  |  | Mixing Damper
Dönüş Damperi |  |  | Bypass Damperi
Return Damper |  |  | By-Pass Damper
FİLTRELER / FILTERS |  |  | NOT / NOTE
Form-550
| OTOMASYON TEST RAPORU AUTOMATION TEST REPORT |  |  |  | Doküman No Document Number | Form-550
[5 empty] | Yayın Tarihi Publication Date | 2025-10-10
[5 empty] | Rev. No/Tarih Rev. No/Date | 00/00.00.0000
[5 empty] | Güncelleme Tarihi Update Date | 2025-10-10
[5 empty] | Sayfa No Page Number | 2/2
SENSORLER / SENSORS |  |  |  | Tarih/Date
Taze Hava Sıcaklık Sensörü Fresh Air Temp. Sensor |  |  | Oda Sıcaklık Sensörü Room Temp Sensor
Üfleme Sıcaklık Sensörü Supply Air Temp. Sensor |  |  | Oda Sıcaklık Sensörü 2 Room Temp Sensor 2
Dönüş Sıcaklık Sensörü Return Air Temp. Sensor |  |  | Su Sıcaklık Sensörü Water Temp Sensor
Egzoz Sıcaklık Sensörü Exhaust Air Temp. Sensor |  |  | Dönüş CO2 Sensörü Return CO2 Sensor
Soğutma Sonrası Sıcaklk Sensör AfterCoil Air Temp. Sensor |  |  | Dönüş CO2 Sıcaklık Sensörü Return Air CO2 Temp. Sensor
Karışım Havası Sıcaklk Sensör Mix Air Temp. Sensor
Systemair HSK Havalandırma Endüstri San. Ve Tic. A. Ş.
Genel Müdürlük Yapı Kredi Plaza, Levent Mah, Cömert Sok. No: 1, B Blok, Kat 5, 34330 İstanbul, Türkiye Phone: +90 212 356 40 60 www.systemair.com.tr |  | Fabrika Demirciler Mah, MOSB (Makine Organize Sanayi Bölgesi) 5. Cadde No:5, 41455 Kocaeli, Türkiye Phone: +90 262 460 49 81 www.systemair.com.tr

## ModbusRegister
REGISTER NAME | UNIT | ACTION | DESCRIPTION | INTERVAL
HOLD REGISTER 1 | C | READ | Supply Air Sensor Temp Value | [-100, 100]
HOLD REGISTER 2 | %rH | READ | Supply Air Sensor Hum Value | [0, 100]
HOLD REGISTER 3 | ppm | READ | Supply Air Sensor CO2 Value | [0, 2000]
HOLD REGISTER 4 | kJ/kg | READ | Supply Air Sensor Entropy Value | [0, 2000]
HOLD REGISTER 5 | g/kg | READ | Supply Air Sensor ABS Hum Value | [0, 2000]
HOLD REGISTER 95 | 0=Normal, 1=Alarm | READ | Supply Air Sensor Comm Alarm | [0, 1]
HOLD REGISTER 6 | C | READ | Return Air Sensor Temp Value | [-100, 100]
HOLD REGISTER 7 | %rH | READ | Return Air Sensor Hum Value | [0, 100]
HOLD REGISTER 8 | ppm | READ | Return Air Sensor CO2 Value | [0, 2000]
HOLD REGISTER 9 | kJ/kg | READ | Return Air Sensor Entropy Value | [0, 2000]
HOLD REGISTER 10 | g/kg | READ | Return Air Sensor ABS Hum Value | [0, 2000]
HOLD REGISTER 96 | 0=Normal, 1=Alarm | READ | Return Air Sensor Comm Alarm | [0, 1]
HOLD REGISTER 11 | c | READ | Fresh Air Sensor Temp Value | [-100, 100]
HOLD REGISTER 12 | %rH | READ | Fresh Air Sensor Hum Value | [0, 100]
HOLD REGISTER 13 | ppm | READ | Fresh Air Sensor CO2 Value | [0, 2000]
HOLD REGISTER 14 | kJ/kg | READ | Fresh Air Sensor Entropy Value | [0, 2000]
HOLD REGISTER 15 | g/kg | READ | Fresh Air Sensor ABS Hum Value | [0, 2000]
HOLD REGISTER 97 | 0=Normal, 1=Alarm | READ | Fresh Air Sensor Comm Alarm | [0, 1]
HOLD REGISTER 16 | C | READ | AfterCoil Air Sensor Temp Value | [-100, 100]
HOLD REGISTER 17 | %rH | READ | AfterCoil Air Sensor Hum Value | [0, 100]
HOLD REGISTER 18 | ppm | READ | AfterCoil Air Sensor CO2 Value | [0, 2000]
HOLD REGISTER 99 | 0=Normal, 1=Alarm | READ | After Coil Air Sensor Comm Alarm | [0, 1]
HOLD REGISTER 19 | C | READ | Exhaust Air Sensor Temp Value | [-100, 100]
HOLD REGISTER 20 | %rH | READ | Exhaust Air Sensor Hum Value | [0, 100]
HOLD REGISTER 21 | ppm | READ | Exhaust Air Sensor CO2 Value | [0, 2000]
HOLD REGISTER 98 | 0=Normal, 1=Alarm | READ | Exhaust Air Sensor Comm Alarm | [0, 1]
HOLD REGISTER 22 | ppm | READ | Return CO2 Sensor CO2 Value | [0, 2000]
HOLD REGISTER 23 | C | READ | Room Sensor Temp Value | [-100, 100]
HOLD REGISTER 24 | %rH | READ | Room Sensor Hum Value | [0, 100]
HOLD REGISTER 25 | C | READ | Water Sensor Temp Value | [-100, 100]
HOLD REGISTER 26 | C | READ | Room Sensor 2 Temp Value | [-100, 100]
HOLD REGISTER 27 | C | READ | Mix Air Sensor Temp Value | [-100, 100]
HOLD REGISTER 28 | % | READ | Mix Air Sensor Hum Value | [0, 100]
HOLD REGISTER 29 | PPM | READ | Mix Air Sensor CO2 Value | [0, 2000]
HOLD REGISTER 90 | 0=Normal, 1=Alarm | READ | Mix Air Sensor Comm Alarm | [0, 1]
HOLD REGISTER 30 | C | READ | Return CO2 Air Sensor Temp Value | [-100, 100]
HOLD REGISTER 31 | PPM | READ | Return CO2 Air Sensor CO2 Value | [0, 2000]
HOLD REGISTER 91 | 0=Normal, 1=Alarm | READ | Return CO2 Air Sensor Comm Alarm | [0, 1]
HOLD REGISTER 36 | 0=Off, 1=On | WRITE | Temp Average Room Sensor 1 EN | [0, 1]
HOLD REGISTER 37 | 0=Off, 1=On | WRITE | Temp Average Room Sensor 2 EN | [0, 1]
HOLD REGISTER 38 | 0=Off, 1=On | WRITE | Temp Average Room Sensor 3 EN | [0, 1]
HOLD REGISTER 39 | 0=Off, 1=On | WRITE | Temp Average Room Sensor 4 EN | [0, 1]
HOLD REGISTER 40 | C | READ | Temp Average Temp Average | [-64, 64]
HOLD REGISTER 41 | C | WRITE | Room Temp From Bms | [-64, 64]
HOLD REGISTER 42 | % | WRITE | Room Hum From Bms | [0, 100]
HOLD REGISTER 43 | C | WRITE | Fresh Temp From Bms | [-64, 64]
HOLD REGISTER 45 | rpm | READ | SAF EBM 1 RPM | [0, 1000]
HOLD REGISTER 46 | kW | READ | SAF EBM 1 Power | [0, 100000]
HOLD REGISTER 47 | A | READ | SAF EBM 1 Current | [-64, 64]
HOLD REGISTER 48 | C | READ | SAF EBM 1 Motor Temp | [-1000, 1000]
HOLD REGISTER 49 | h | READ | SAF EBM 1 Motor Run Hour | [0, 10000000]
HOLD REGISTER 110 | 0=Normal, 1=Alarm | READ | SAF EBM 1 Motor Alarm | [0, 1]
HOLD REGISTER 116 | 0=Normal, 1=Alarm | READ | SAF EBM 1 Comm Alarm | [0, 1]
HOLD REGISTER 122 | 0=Normal, 1=Alarm | READ | SAF EBM 1 Motor Warning | [0, 1]
HOLD REGISTER 51 | rpm | READ | SAF EBM 2 RPM | [0, 1000]
HOLD REGISTER 52 | kW | READ | SAF EBM 2 Power | [0, 100000]
HOLD REGISTER 53 | A | READ | SAF EBM 2 Current | [-64, 64]
HOLD REGISTER 54 | C | READ | SAF EBM 2 Motor Temp | [-1000, 1000]
HOLD REGISTER 55 | h | READ | SAF EBM 2 Motor Run Hour | [0, 10000000]
HOLD REGISTER 111 | 0=Normal, 1=Alarm | READ | SAF EBM 2 Motor Alarm | [0, 1]
HOLD REGISTER 117 | 0=Normal, 1=Alarm | READ | SAF EBM 2 Comm Alarm | [0, 1]
HOLD REGISTER 123 | 0=Normal, 1=Alarm | READ | SAF EBM 2 Motor Warning | [0, 1]
HOLD REGISTER 57 | rpm | READ | SAF EBM 3 RPM | [0, 1000]
HOLD REGISTER 58 | kW | READ | SAF EBM 3 Power | [0, 100000]
HOLD REGISTER 59 | A | READ | SAF EBM 3 Current | [-64, 64]
HOLD REGISTER 60 | C | READ | SAF EBM 3 Motor Temp | [-1000, 1000]
HOLD REGISTER 61 | h | READ | SAF EBM 3 Motor Run Hour | [0, 10000000]
HOLD REGISTER 112 | 0=Normal, 1=Alarm | READ | SAF EBM 3 Motor Alarm | [0, 1]
HOLD REGISTER 118 | 0=Normal, 1=Alarm | READ | SAF EBM 3 Comm Alarm | [0, 1]
HOLD REGISTER 124 | 0=Normal, 1=Alarm | READ | SAF EBM 3 Motor Warning | [0, 1]
HOLD REGISTER 66 | rpm | READ | EAF EBM 1 RPM | [0, 1000]
HOLD REGISTER 67 | kW | READ | EAF EBM 1 Power | [0, 100000]
HOLD REGISTER 68 | A | READ | EAF EBM 1 Current | [-64, 64]
HOLD REGISTER 69 | C | READ | EAF EBM 1 Motor Temp | [-1000, 1000]
HOLD REGISTER 70 | h | READ | EAF EBM 1 Motor Run Hour | [0, 10000000]
HOLD REGISTER 113 | 0=Normal, 1=Alarm | READ | EAF EBM 1 Motor Alarm | [0, 1]
HOLD REGISTER 119 | 0=Normal, 1=Alarm | READ | EAF EBM 1 Comm Alarm | [0, 1]
HOLD REGISTER 125 | 0=Normal, 1=Alarm | READ | EAF EBM 1 Motor Warning | [0, 1]
HOLD REGISTER 75 | rpm | READ | EAF EBM 2 RPM | [0, 1000]
HOLD REGISTER 76 | kW | READ | EAF EBM 2 Power | [0, 100000]
HOLD REGISTER 77 | A | READ | EAF EBM 2 Current | [-64, 64]
HOLD REGISTER 78 | C | READ | EAF EBM 2 Motor Temp | [-1000, 1000]
HOLD REGISTER 79 | h | READ | EAF EBM 2 Motor Run Hour | [0, 10000000]
HOLD REGISTER 114 | 0=Normal, 1=Alarm | READ | EAF EBM 2 Motor Alarm | [0, 1]
HOLD REGISTER 120 | 0=Normal, 1=Alarm | READ | EAF EBM 2 Comm Alarm | [0, 1]
HOLD REGISTER 126 | 0=Normal, 1=Alarm | READ | EAF EBM 2 Motor Warning | [0, 1]
HOLD REGISTER 84 | rpm | READ | EAF EBM 3 RPM | [0, 1000]
HOLD REGISTER 85 | kW | READ | EAF EBM 3 Power | [0, 100000]
HOLD REGISTER 86 | A | READ | EAF EBM 3 Current | [-64, 64]
HOLD REGISTER 87 | C | READ | EAF EBM 3 Motor Temp | [-1000, 1000]
HOLD REGISTER 88 | h | READ | EAF EBM 3 Motor Run Hour | [0, 10000000]
HOLD REGISTER 115 | 0=Normal, 1=Alarm | READ | EAF EBM 3 Motor Alarm | [0, 1]
HOLD REGISTER 121 | 0=Normal, 1=Alarm | READ | EAF EBM 3 Comm Alarm | [0, 1]
HOLD REGISTER 127 | 0=Normal, 1=Alarm | READ | EAF EBM 3 Motor Warning | [0, 1]
HOLD REGISTER 393 | rpm | READ | ZiehlAbegg Supply 1 RPM | [0, 100000]
HOLD REGISTER 394 | kW | READ | ZiehlAbegg Supply 1 Power | [0, 100000]
HOLD REGISTER 395 | A | READ | ZiehlAbegg Supply 1 Current | [0, 100000]
HOLD REGISTER 128 | 0=Normal, 1=Alarm | READ | ZiehlAbegg Supply 1 Comm Alarm | [0, 1]
HOLD REGISTER 134 | 0=Normal, 1=Alarm | READ | ZiehlAbegg Supply 1 Alarm | [0, 1]
HOLD REGISTER 396 | rpm | READ | ZiehlAbegg Exhaust 1 RPM | [0, 100000]
HOLD REGISTER 397 | kW | READ | ZiehlAbegg Exhaust 1 Power | [0, 100000]
HOLD REGISTER 398 | A | READ | ZiehlAbegg Exhaust 1 Current | [0, 100000]
HOLD REGISTER 131 | 0=Normal, 1=Alarm | READ | ZiehlAbegg Exhaust 1 Comm Alarm | [0, 1]
HOLD REGISTER 137 | 0=Normal, 1=Alarm | READ | ZiehlAbegg Exhaust 1 Alarm | [0, 1]
HOLD REGISTER 399 | rpm | READ | ZiehlAbegg Supply 2 RPM | [0, 100000]
HOLD REGISTER 400 | kW | READ | ZiehlAbegg Supply 2 Power | [0, 100000]
HOLD REGISTER 401 | A | READ | ZiehlAbegg Supply 2 Current | [0, 100000]
HOLD REGISTER 129 | 0=Normal, 1=Alarm | READ | ZiehlAbegg Supply 2 Comm Alarm | [0, 1]
HOLD REGISTER 135 | 0=Normal, 1=Alarm | READ | ZiehlAbegg Supply 2 Alarm | [0, 1]
HOLD REGISTER 402 | rpm | READ | ZiehlAbegg Exhaust 2 RPM | [0, 100000]
HOLD REGISTER 403 | kW | READ | ZiehlAbegg Exhaust 2 Power | [0, 100000]
HOLD REGISTER 404 | A | READ | ZiehlAbegg Exhaust 2 Current | [0, 100000]
HOLD REGISTER 132 | 0=Normal, 1=Alarm | READ | ZiehlAbegg Exhaust 2 Comm Alarm | [0, 1]
HOLD REGISTER 138 | 0=Normal, 1=Alarm | READ | ZiehlAbegg Exhaust 2 Alarm | [0, 1]
HOLD REGISTER 405 | rpm | READ | ZiehlAbegg Supply 3 RPM | [0, 100000]
HOLD REGISTER 406 | kW | READ | ZiehlAbegg Supply 3 Power | [0, 100000]
HOLD REGISTER 407 | A | READ | ZiehlAbegg Supply 3 Current | [0, 100000]
HOLD REGISTER 130 | 0=Normal, 1=Alarm | READ | ZiehlAbegg Supply 3 Comm Alarm | [0, 1]
HOLD REGISTER 136 | 0=Normal, 1=Alarm | READ | ZiehlAbegg Supply 3 Alarm | [0, 1]
HOLD REGISTER 408 | rpm | READ | ZiehlAbegg Exhaust 3 RPM | [0, 100000]
HOLD REGISTER 409 | kW | READ | ZiehlAbegg Exhaust 3 Power | [0, 100000]
HOLD REGISTER 410 | A | READ | ZiehlAbegg Exhaust 3 Current | [0, 100000]
HOLD REGISTER 133 | 0=Normal, 1=Alarm | READ | ZiehlAbegg Exhaust 3 Comm Alarm | [0, 1]
HOLD REGISTER 139 | 0=Normal, 1=Alarm | READ | ZiehlAbegg Exhaust 3 Alarm | [0, 1]
HOLD REGISTER 332 | 0=Stopped, 1=Running | READ | FC101Vant1 FCRunning | [0, 1]
HOLD REGISTER 333 | 0=Busy, 1=Ready | READ | FC101Vant1 FCReady | [0, 1]
HOLD REGISTER 334 | A | READ | FC101Vant1 Current Valve | [0, 100000]
HOLD REGISTER 335 | Hz | READ | FC101Vant1 Hertz Valve | [0, 100000]
HOLD REGISTER 336 | rpm | READ | FC101Vant1 RPM Valve | [0, 100000]
HOLD REGISTER 337 | kW | READ | FC101Vant1 kW Valve | [0, 100000]
HOLD REGISTER 338 | V | READ | FC101Vant1 Volt Valve | [0, 100000]
HOLD REGISTER 339 | t | READ | FC101Vant1 Torque Valve | [0, 100000]
HOLD REGISTER 340 | Hz | READ | FC101Vant1 Min Referance | [0, 100000]
HOLD REGISTER 341 | Hz | READ | FC101Vant1 Max Referance | [0, 100000]
HOLD REGISTER 342 | h | READ | FC101Vant1 Running Hour | [0, 100000]
HOLD REGISTER 343 | h | READ | FC101Vant1 Operation Hour | [0, 100000]
HOLD REGISTER 344 |  | READ | FC101Vant1 kWh Counter | [0, 100000]
HOLD REGISTER 345 | 0=HandOn,1=Auto | READ | FC101Vant1 FCAuto Mode | [0, 1]
HOLD REGISTER 346 | 0=NotReady,1=Ready | READ | FC101Vant1 Control Ready | [0, 1]
HOLD REGISTER 102 | 0=Normal, 1=Alarm | READ | FC101Vant 1 Comm Alarm | [0, 1]
HOLD REGISTER 106 | 0=Normal, 1=Alarm | READ | FC101Vant 1 FCAlarm | [0, 1]
HOLD REGISTER 348 | 0=Off, 1=On | READ | FC101Vant2 FCRunning | [0, 1]
HOLD REGISTER 349 | 0=Off, 1=On | READ | FC101Vant2 FCReady | [0, 1]
HOLD REGISTER 350 | A | READ | FC101Vant2 Current Valve | [0, 100000]
HOLD REGISTER 351 | Hz | READ | FC101Vant2 Hertz Valve | [0, 100000]
HOLD REGISTER 352 | rpm | READ | FC101Vant2 RPM Valve | [0, 100000]
HOLD REGISTER 353 | kW | READ | FC101Vant2 kW Valve | [0, 100000]
HOLD REGISTER 354 | V | READ | FC101Vant2 Volt Valve | [0, 100000]
HOLD REGISTER 355 | t | READ | FC101Vant2 Torque Valve | [0, 100000]
HOLD REGISTER 356 | Hz | READ | FC101Vant2 Min Referance | [0, 100000]
HOLD REGISTER 357 | Hz | READ | FC101Vant2 Max Referance | [0, 100000]
HOLD REGISTER 358 | h | READ | FC101Vant2 Running Hour | [0, 100000]
HOLD REGISTER 359 | h | READ | FC101Vant2 Operation Hour | [0, 100000]
HOLD REGISTER 360 |  | READ | FC101Vant2 kWh Counter | [0, 100000]
HOLD REGISTER 361 | 0=HandOn,1=Auto | READ | FC101Vant2 FCAuto Mode | [0, 1]
HOLD REGISTER 362 | 0=NotReady,1=Ready | READ | FC101Vant2 Control Ready | [0, 1]
HOLD REGISTER 103 | 0=Normal, 1=Alarm | READ | FC101Vant 2 Comm Alarm | [0, 1]
HOLD REGISTER 107 | 0=Normal, 1=Alarm | READ | FC101Vant 2 FCAlarm | [0, 1]
HOLD REGISTER 363 | 0=Off, 1=On | READ | FC101Asp1 FCRunning | [0, 1]
HOLD REGISTER 364 | 0=Off, 1=On | READ | FC101Asp1 FCReady | [0, 1]
HOLD REGISTER 365 | A | READ | FC101Asp1 Current Valve | [0, 100000]
HOLD REGISTER 366 | Hz | READ | FC101Asp1 Hertz Valve | [0, 100000]
HOLD REGISTER 367 | rpm | READ | FC101Asp1 RPM Valve | [0, 100000]
HOLD REGISTER 368 | kW | READ | FC101Asp1 kW Valve | [0, 100000]
HOLD REGISTER 369 | V | READ | FC101Asp1 Volt Valve | [0, 100000]
HOLD REGISTER 370 | t | READ | FC101Asp1 Torque Valve | [0, 100000]
HOLD REGISTER 371 | Hz | READ | FC101Asp1 Min Referance | [0, 100000]
HOLD REGISTER 372 | Hz | READ | FC101Asp1 Max Referance | [0, 100000]
HOLD REGISTER 373 | h | READ | FC101Asp1 Running Hour | [0, 100000]
HOLD REGISTER 374 | h | READ | FC101Asp1 Operation Hour | [0, 100000]
HOLD REGISTER 375 |  | READ | FC101Asp1 kWh Counter | [0, 100000]
HOLD REGISTER 376 | 0=HandOn,1=Auto | READ | FC101Asp1 FCAuto Mode | [0, 1]
HOLD REGISTER 377 | 0=NotReady,1=Ready | READ | FC101Asp1 Control Ready | [0, 1]
HOLD REGISTER 104 | 0=Normal, 1=Alarm | READ | FC101Asp 1 Comm Alarm | [0, 1]
HOLD REGISTER 108 | 0=Normal, 1=Alarm | READ | FC101Asp 1 FCAlarm | [0, 1]
HOLD REGISTER 378 | 0=Off, 1=On | READ | FC101Asp2 FCRunning | [0, 1]
HOLD REGISTER 379 | 0=Off, 1=On | READ | FC101Asp2 FCReady | [0, 1]
HOLD REGISTER 380 | A | READ | FC101Asp2 Current Valve | [0, 100000]
HOLD REGISTER 381 | Hz | READ | FC101Asp2 Hertz Valve | [0, 100000]
HOLD REGISTER 382 | rpm | READ | FC101Asp2 RPM Valve | [0, 100000]
HOLD REGISTER 383 | kW | READ | FC101Asp2 kW Valve | [0, 100000]
HOLD REGISTER 384 | V | READ | FC101Asp2 Volt Valve | [0, 100000]
HOLD REGISTER 385 | t | READ | FC101Asp2 Torque Valve | [0, 100000]
HOLD REGISTER 386 | Hz | READ | FC101Asp2 Min Referance | [0, 100000]
HOLD REGISTER 387 | Hz | READ | FC101Asp2 Max Referance | [0, 100000]
HOLD REGISTER 388 | h | READ | FC101Asp2 Running Hour | [0, 100000]
HOLD REGISTER 389 | h | READ | FC101Asp2 Operation Hour | [0, 100000]
HOLD REGISTER 390 |  | READ | FC101Asp2 kWh Counter | [0, 100000]
HOLD REGISTER 391 | 0=HandOn,1=Auto | READ | FC101Asp2 FCAuto Mode | [0, 1]
HOLD REGISTER 392 | 0=NotReady,1=Ready | READ | FC101Asp2 Control Ready | [0, 1]
HOLD REGISTER 105 | 0=Normal, 1=Alarm | READ | FC101Asp 2 Comm Alarm | [0, 1]
HOLD REGISTER 109 | 0=Normal, 1=Alarm | READ | FC101Asp 2 FCAlarm | [0, 1]
HOLD REGISTER 140 | 0=Normal, 1=Alarm | READ | DX Alarm 1 | [0, 1]
HOLD REGISTER 145 | 0=Normal, 1=Alarm | READ | DX Defrost 1 | [0, 1]
HOLD REGISTER 141 | 0=Normal, 1=Alarm | READ | DX Alarm 2 | [0, 1]
HOLD REGISTER 146 | 0=Normal, 1=Alarm | READ | DX Defrost 2 | [0, 1]
HOLD REGISTER 142 | 0=Normal, 1=Alarm | READ | DX Alarm 3 | [0, 1]
HOLD REGISTER 147 | 0=Normal, 1=Alarm | READ | DX Defrost 3 | [0, 1]
HOLD REGISTER 143 | 0=Normal, 1=Alarm | READ | DX Alarm 4 | [0, 1]
HOLD REGISTER 148 | 0=Normal, 1=Alarm | READ | DX Defrost 4 | [0, 1]
HOLD REGISTER 144 | 0=Normal, 1=Alarm | READ | DX Alarm 5 | [0, 1]
HOLD REGISTER 149 | 0=Normal, 1=Alarm | READ | DX Defrost 5 | [0, 1]
HOLD REGISTER 565 | 0-100% | READ | DX Capacity Value | [-64, 64]
HOLD REGISTER 566 | 0=Off, 1=On | READ | DX Status | [0, 1]
HOLD REGISTER 567 | 0=Off, 1=Cool, 2=Heat, 3=Dehum | READ | DX Mode | [0, 3]
HOLD REGISTER 92 | 0=Normal, 1=Alarm reset | WRITE | Alarm Reset | [0, 1]
HOLD REGISTER 156 | 0=Normal, 1=Alarm | READ | Fresh F7 Filter Alarm | [0, 1]
HOLD REGISTER 155 | 0=Normal, 1=Alarm | READ | Fresh G4 Filter Alarm | [0, 1]
HOLD REGISTER 161 | 0=Normal, 1=Alarm | READ | Return G4 Filter Alarm | [0, 1]
HOLD REGISTER 168 | 0=Normal, 1=Alarm | READ | Supply F9 Filter Alarm | [0, 1]
HOLD REGISTER 157 | 0=Normal, 1=Alarm | READ | Fresh F9 Filter Alarm | [0, 1]
HOLD REGISTER 162 | 0=Normal, 1=Alarm | READ | Return F7 Filter Alarm | [0, 1]
HOLD REGISTER 154 | 0=Normal, 1=Alarm | READ | Fresh M5 Filter Alarm | [0, 1]
HOLD REGISTER 158 | 0=Normal, 1=Alarm | READ | Fresh G2 Filter Alarm | [0, 1]
HOLD REGISTER 159 | 0=Normal, 1=Alarm | READ | Fresh F4 Filter Alarm | [0, 1]
HOLD REGISTER 160 | 0=Normal, 1=Alarm | READ | Return M5 Filter Alarm | [0, 1]
HOLD REGISTER 163 | 0=Normal, 1=Alarm | READ | Return F9 Filter Alarm | [0, 1]
HOLD REGISTER 164 | 0=Normal, 1=Alarm | READ | Return G2 Filter Alarm | [0, 1]
HOLD REGISTER 165 | 0=Normal, 1=Alarm | READ | Supply M5 Filter Alarm | [0, 1]
HOLD REGISTER 166 | 0=Normal, 1=Alarm | READ | Supply G4 Filter Alarm | [0, 1]
HOLD REGISTER 167 | 0=Normal, 1=Alarm | READ | Supply F7 Filter Alarm | [0, 1]
HOLD REGISTER 169 | 0=Normal, 1=Alarm | READ | Supply G2 Filter Alarm | [0, 1]
HOLD REGISTER 170 | 0=Normal, 1=Alarm | READ | Hepa Filter Alarm | [0, 1]
HOLD REGISTER 171 | 0=Normal, 1=Alarm | READ | H13 Filter Alarm | [0, 1]
HOLD REGISTER 172 | 0=Normal, 1=Alarm | READ | EMERGENCY | [0, 1]
HOLD REGISTER 173 | 0=Normal, 1=Alarm | READ | FIRE ALARM | [0, 1]
HOLD REGISTER 174 | 0=Normal, 1=Alarm | READ | PHASE ALARM | [0, 1]
HOLD REGISTER 175 | 0=Normal, 1=Alarm | READ | VANT DOOR SW | [0, 1]
HOLD REGISTER 176 | 0=Normal, 1=Alarm | READ | ASP DOOR SW | [0, 1]
HOLD REGISTER 177 | 0=Normal, 1=Alarm | READ | FROST ALARM | [0, 1]
HOLD REGISTER 440 | 0-100% | READ | Bypass Damper Position | [0, 100]
HOLD REGISTER 443 | 0=ManuelStop, 1=Maneul, 2=Auto | WRITE | Bypass Mode Select Local BMS | [0, 2]
HOLD REGISTER 444 | 0-100% | WRITE | Bypass Manuel Set Local BMS | [0, 100]
HOLD REGISTER 445 | -5 25 C | WRITE | Bypass Set Local BMS | [-5, 25]
HOLD REGISTER 446 | 0=Off, 1=On | WRITE | Bypass Recover Mod | [0, 1]
HOLD REGISTER 441 | 0-100% | READ | Bypass Damper 1 Feedback | [0, 100]
HOLD REGISTER 219 | 0=Normal, 1=Alarm | READ | Bypass Damper 1 Comm Alarm | [0, 1]
HOLD REGISTER 220 | 0=Normal, 1=Alarm | READ | Bypass Damper 1 Feedback Alarm | [0, 1]
HOLD REGISTER 247 | 0=Normal, 1=Alarm | READ | Bypass Damper 1 Mechanical Fault | [0, 1]
HOLD REGISTER 442 | 0-100% | READ | Bypass Damper 2 Feedback | [0, 100]
HOLD REGISTER 221 | 0=Normal, 1=Alarm | READ | Bypass Damper 2 Comm Alarm | [0, 1]
HOLD REGISTER 222 | 0=Normal, 1=Alarm | READ | Bypass Damper 2 Feedback Alarm | [0, 1]
HOLD REGISTER 248 | 0=Normal, 1=Alarm | READ | Bypass Damper 2 Mechanical Fault | [0, 1]
HOLD REGISTER 413 | 0-100% | READ | Supply Damper Position | [0, 100]
HOLD REGISTER 414 | 0-100% | READ | Supply Damper 1 Feedback | [0, 100]
HOLD REGISTER 187 | 0=Normal, 1=Alarm | READ | Supply Damper 1 Comm Alarm | [0, 1]
HOLD REGISTER 188 | 0=Normal, 1=Alarm | READ | Supply Damper 1 Feedback Alarm | [0, 1]
HOLD REGISTER 231 | 0=Normal, 1=Alarm | READ | Supply Damper 1 Mechanical Fault | [0, 1]
HOLD REGISTER 415 | 0-100% | READ | Supply Damper 2 Feedback | [0, 100]
HOLD REGISTER 189 | 0=Normal, 1=Alarm | READ | Supply Damper 2 Comm Alarm | [0, 1]
HOLD REGISTER 190 | 0=Normal, 1=Alarm | READ | Supply Damper 2 Feedback Alarm | [0, 1]
HOLD REGISTER 232 | 0=Normal, 1=Alarm | READ | Supply Damper 2 Mechanical Fault | [0, 1]
HOLD REGISTER 416 | 0-100% | READ | Supply Damper 3 Feedback | [0, 100]
HOLD REGISTER 191 | 0=Normal, 1=Alarm | READ | Supply Damper 3 Comm Alarm | [0, 1]
HOLD REGISTER 192 | 0=Normal, 1=Alarm | READ | Supply Damper 3 Feedback Alarm | [0, 1]
HOLD REGISTER 233 | 0=Normal, 1=Alarm | READ | Supply Damper 3 Mechanical Fault | [0, 1]
HOLD REGISTER 417 | 0-100% | READ | Supply Damper 4 Feedback | [0, 100]
HOLD REGISTER 193 | 0=Normal, 1=Alarm | READ | Supply Damper 4 Comm Alarm | [0, 1]
HOLD REGISTER 194 | 0=Normal, 1=Alarm | READ | Supply Damper 4 Feedback Alarm | [0, 1]
HOLD REGISTER 234 | 0=Normal, 1=Alarm | READ | Supply Damper 4 Mechanical Fault | [0, 1]
HOLD REGISTER 418 | 0-100% | READ | Fresh Damper Position | [0, 100]
HOLD REGISTER 419 | 0-100% | READ | Fresh Damper 1 Feedback | [0, 100]
HOLD REGISTER 195 | 0=Normal, 1=Alarm | READ | Fresh Damper 1 Comm Alarm | [0, 1]
HOLD REGISTER 196 | 0=Normal, 1=Alarm | READ | Fresh Damper 1 Feedback Alarm | [0, 1]
HOLD REGISTER 227 | 0=Normal, 1=Alarm | READ | Fresh Damper 1 Mechanical Fault | [0, 1]
HOLD REGISTER 420 | 0-100% | READ | Fresh Damper 2 Feedback | [0, 100]
HOLD REGISTER 197 | 0=Normal, 1=Alarm | READ | Fresh Damper 2 Comm Alarm | [0, 1]
HOLD REGISTER 198 | 0=Normal, 1=Alarm | READ | Fresh Damper 2 Feedback Alarm | [0, 1]
HOLD REGISTER 228 | 0=Normal, 1=Alarm | READ | Fresh Damper 2 Mechanical Fault | [0, 1]
HOLD REGISTER 420 | 0-100% | READ | Fresh Damper 3 Feedback | [0, 100]
HOLD REGISTER 199 | 0=Normal, 1=Alarm | READ | Fresh Damper 3 Comm Alarm | [0, 1]
HOLD REGISTER 200 | 0=Normal, 1=Alarm | READ | Fresh Damper 3 Feedback Alarm | [0, 1]
HOLD REGISTER 229 | 0=Normal, 1=Alarm | READ | Fresh Damper 3 Mechanical Fault | [0, 1]
HOLD REGISTER 420 | 0-100% | READ | Fresh Damper 4 Feedback | [0, 100]
HOLD REGISTER 201 | 0=Normal, 1=Alarm | READ | Fresh Damper 4 Comm Alarm | [0, 1]
HOLD REGISTER 202 | 0=Normal, 1=Alarm | READ | Fresh Damper 4 Feedback Alarm | [0, 1]
HOLD REGISTER 230 | 0=Normal, 1=Alarm | READ | Fresh Damper 4 Mechanical Fault | [0, 1]
HOLD REGISTER 420 | 0-100% | READ | Return Damper Position | [0, 100]
HOLD REGISTER 424 | 0-100% | READ | Return Damper 1 Feedback | [0, 100]
HOLD REGISTER 203 | 0=Normal, 1=Alarm | READ | Return Damper 1 Comm Alarm | [0, 1]
HOLD REGISTER 204 | 0=Normal, 1=Alarm | READ | Return Damper 1 Feedback Alarm | [0, 1]
HOLD REGISTER 235 | 0=Normal, 1=Alarm | READ | Return Damper 1 Mechanical Fault | [0, 1]
HOLD REGISTER 425 | 0-100% | READ | Return Damper 2 Feedback | [0, 100]
HOLD REGISTER 205 | 0=Normal, 1=Alarm | READ | Return Damper 2 Comm Alarm | [0, 1]
HOLD REGISTER 206 | 0=Normal, 1=Alarm | READ | Return Damper 2 Feedback Alarm | [0, 1]
HOLD REGISTER 236 | 0=Normal, 1=Alarm | READ | Return Damper 2 Mechanical Fault | [0, 1]
HOLD REGISTER 426 | 0-100% | READ | Return Damper 3 Feedback | [0, 100]
HOLD REGISTER 207 | 0=Normal, 1=Alarm | READ | Return Damper 3 Comm Alarm | [0, 1]
HOLD REGISTER 208 | 0=Normal, 1=Alarm | READ | Return Damper 3 Feedback Alarm | [0, 1]
HOLD REGISTER 237 | 0=Normal, 1=Alarm | READ | Return Damper 3 Mechanical Fault | [0, 1]
HOLD REGISTER 427 | 0-100% | READ | Return Damper 4 Feedback | [0, 100]
HOLD REGISTER 209 | 0=Normal, 1=Alarm | READ | Return Damper 4 Comm Alarm | [0, 1]
HOLD REGISTER 210 | 0=Normal, 1=Alarm | READ | Return Damper 4 Feedback Alarm | [0, 1]
HOLD REGISTER 238 | 0=Normal, 1=Alarm | READ | Return Damper 4 Mechanical Fault | [0, 1]
HOLD REGISTER 428 | 0-100% | READ | Exhaust Damper Position | [0, 100]
HOLD REGISTER 429 | 0-100% | READ | Exhaust Damper 1 Feedback | [0, 100]
HOLD REGISTER 211 | 0=Normal, 1=Alarm | READ | Exhaust Damper 1 Comm Alarm | [0, 1]
HOLD REGISTER 212 | 0=Normal, 1=Alarm | READ | Exhaust Damper 1 Feedback Alarm | [0, 1]
HOLD REGISTER 239 | 0=Normal, 1=Alarm | READ | Exhaust Damper 1 Mechanical Fault | [0, 1]
HOLD REGISTER 430 | 0-100% | READ | Exhaust Damper 2 Feedback | [0, 100]
HOLD REGISTER 213 | 0=Normal, 1=Alarm | READ | Exhaust Damper 2 Comm Alarm | [0, 1]
HOLD REGISTER 214 | 0=Normal, 1=Alarm | READ | Exhaust Damper 2 Feedback Alarm | [0, 1]
HOLD REGISTER 240 | 0=Normal, 1=Alarm | READ | Exhaust Damper 2 Mechanical Fault | [0, 1]
HOLD REGISTER 431 | 0-100% | READ | Exhaust Damper 3 Feedback | [0, 100]
HOLD REGISTER 215 | 0=Normal, 1=Alarm | READ | Exhaust Damper 3 Comm Alarm | [0, 1]
HOLD REGISTER 216 | 0=Normal, 1=Alarm | READ | Exhaust Damper 3 Feedback Alarm | [0, 1]
HOLD REGISTER 241 | 0=Normal, 1=Alarm | READ | Exhaust Damper 3 Mechanical Fault | [0, 1]
HOLD REGISTER 432 | 0-100% | READ | Exhaust Damper 4 Feedback | [0, 100]
HOLD REGISTER 217 | 0=Normal, 1=Alarm | READ | Exhaust Damper 4 Comm Alarm | [0, 1]
HOLD REGISTER 218 | 0=Normal, 1=Alarm | READ | Exhaust Damper 4 Feedback Alarm | [0, 1]
HOLD REGISTER 242 | 0=Normal, 1=Alarm | READ | Exhaust Damper 4 Mechanical Fault | [0, 1]
HOLD REGISTER 320 | 0=ManuelStop, 1=Maneul, 2=Auto | WRITE | Damper Auto Manuel Select BMS | [0, 2]
HOLD REGISTER 321 | 0-100% | WRITE | Damper Min Referance BMS | [0, 100]
HOLD REGISTER 322 | 0-100% | WRITE | Damper Manuel Referance BMS | [0, 100]
HOLD REGISTER 323 | ppm | WRITE | Damper CO2 Set BMS | [0, 2000]
HOLD REGISTER 324 | ppm | WRITE | Damper CO2 Deadband BMS
HOLD REGISTER 325 | 0-100% | READ | Damper PID
HOLD REGISTER 326 | 0=Temp + CO2 , 1=CO2 | WRITE | Damper Control Type Select | [0, 1]
HOLD REGISTER 433 | 0-100% | READ | Mix Damper Position | [0, 100]
HOLD REGISTER 434 | 0-100% | READ | Mix Damper 1 Feedback | [0, 100]
HOLD REGISTER 223 | 0=Normal, 1=Alarm | READ | Mix Damper 1 Comm Alarm | [0, 1]
HOLD REGISTER 224 | 0=Normal, 1=Alarm | READ | Mix Damper 1 Feedback Alarm | [0, 1]
HOLD REGISTER 243 | 0=Normal, 1=Alarm | READ | Mix Damper 1 Mechanical Fault | [0, 1]
HOLD REGISTER 435 | 0-100% | READ | Mix Damper 2 Feedback | [0, 100]
HOLD REGISTER 225 | 0=Normal, 1=Alarm | READ | Mix Damper 2 Comm Alarm | [0, 1]
HOLD REGISTER 226 | 0=Normal, 1=Alarm | READ | Mix Damper 2 Feedback Alarm | [0, 1]
HOLD REGISTER 244 | 0=Normal, 1=Alarm | READ | Mix Damper 2 Mechanical Fault | [0, 1]
HOLD REGISTER 436 | 0-100% | READ | Mix Damper 3 Feedback | [0, 100]
HOLD REGISTER 245 | 0=Normal, 1=Alarm | READ | Mix Damper 3 Mechanical Fault | [0, 1]
HOLD REGISTER 437 | 0-100% | READ | Mix Damper 4 Feedback | [0, 100]
HOLD REGISTER 246 | 0=Normal, 1=Alarm | READ | Mix Damper 4 Mechanical Fault | [0, 1]
HOLD REGISTER 282 | 0=Local, 1=Bms , 2=Schedule | WRITE | AHU BMS Mod EN | [0, 2]
HOLD REGISTER 283 | 0 = Off, 1= Start | WRITE | AHU BMS Start | [0, 1]
HOLD REGISTER 284 | 0 = Off, 1= Run | READ | AHU Run Status | [0, 1]
HOLD REGISTER 285 | 0 = Off, 1= Start | WRITE | AHU Local Start | [0, 1]
HOLD REGISTER 288 | 0-100% | READ | Heating Valve 1 Feedback | [0, 100]
HOLD REGISTER 289 | 0-100% | READ | Cooling Valve 1 Feedback | [0, 100]
HOLD REGISTER 290 | 0=Supply, 1=Return | WRITE | Temp Control Select BMS | [0, 1]
HOLD REGISTER 291 | 0-100% | READ | Cooling Valve Position | [0, 100]
HOLD REGISTER 292 | 0-100% | READ | Heating Valve Position | [0, 100]
HOLD REGISTER 293 | 0-100% | READ | Heating Valve 2 Feedback | [0, 100]
HOLD REGISTER 294 | 0-100% | READ | Cooling Valve 2 Feedback | [0, 100]
HOLD REGISTER 295 | 10-80 C | WRITE | Temp Set BMS | [10, 80]
HOLD REGISTER 296 | return mode min supply set | WRITE | Supply Min Temp BMS | [10, 80]
HOLD REGISTER 297 | return mode max supply set | WRITE | Supply Max Temp BMS | [10, 80]
HOLD REGISTER 298 | 0=Off, 1=Maneul, 2=Auto | WRITE | Cooling Valve Mode Select BMS | [0, 3]
HOLD REGISTER 299 | 0-100% | WRITE | Cooling Valve Manuel Referance BMS | [0, 100]
HOLD REGISTER 300 | 0=Off, 1=Maneul, 2=Auto | WRITE | Heating Valve Mode Select BMS | [0, 3]
HOLD REGISTER 301 | 0-100% | WRITE | Heating Valve Manuel Referance BMS | [0, 100]
HOLD REGISTER 302 | 0=Off, 1=On | READ | Cooling Mode Active | [0, 1]
HOLD REGISTER 303 | 0=Off, 1=On | READ | Heating Mode Active | [0, 1]
HOLD REGISTER 304 | C | READ | Heat Calculated Temp Set | [-64, 64]
HOLD REGISTER 305 | C | READ | Cool Calculated Temp Set | [-64, 64]
HOLD REGISTER 329 |  | READ | BMS Check Read | [0, 1]
HOLD REGISTER 330 |  | WRITE | BMS Check Write | [0, 1]
HOLD REGISTER 306 | 0=Off, 1=On | READ | Electrical Heater 1 Run | [0, 1]
HOLD REGISTER 307 | 0=Off, 1=On | READ | Electrical Heater 2 Run | [0, 1]
HOLD REGISTER 308 | 0=Off, 1=On | READ | Electrical Heater 3 Run | [0, 1]
HOLD REGISTER 309 | 0=Off,1=1.Stage,2=2.Stage,3=3.Stage | READ | Electrical Heater Stage | [0, 3]
HOLD REGISTER 186 | 0=Normal, 1=Alarm | READ | Electrical Heater High Temp Alarm | [0, 1]
HOLD REGISTER 451 | 0=ManuelStop, 1=Maneul, 2=Auto | WRITE | Rotor Mode Select BMS | [0, 2]
HOLD REGISTER 452 | 0-100% | WRITE | Rotor Manuel Set BMS | [0, 100]
HOLD REGISTER 453 | 0-100% | WRITE | Rotor Max Speed | [0, 100]
HOLD REGISTER 454 | 0-100% | READ | Rotor Position | [0, 100]
HOLD REGISTER 455 | 0=Off, 1=On | READ | Rotor Active | [0, 1]
HOLD REGISTER 150 | 0=Normal, 1=Alarm | READ | Rotor Alarm | [0, 1]
HOLD REGISTER 448 | 0=ManuelStop, 1=Maneul, 2=Auto | WRITE | RunAround Mode Select BMS | [0, 2]
HOLD REGISTER 449 | 0=Off, 1=On | READ | RunAround Start | [0, 1]
HOLD REGISTER 249 | 0=Normal, 1=Alarm | READ | RunAround Water Frost Alarm | [0, 1]
HOLD REGISTER 250 | 0=Normal, 1=Alarm | READ | RunAround Error | [0, 1]
HOLD REGISTER 460 | 0-100% | WRITE | SAF Manuel Referance BMS | [0, 100]
HOLD REGISTER 461 | 0-100% | READ | SAF Actual Manuel Referance | [0, 100]
HOLD REGISTER 462 | 0=ManuelStop, 1=Maneul, 2=Auto | WRITE | SAF Mode Select BMS | [0, 2]
HOLD REGISTER 463 | 0=ManuelStop, 1=Maneul, 2=Auto | READ | SAF Actual Mode | [0, 2]
HOLD REGISTER 464 | m3/h | WRITE | SAF Air Volume Set BMS | [0, 60000]
HOLD REGISTER 465 | m3/h | READ | SAF Actual Air Vol Set | [0, 40000]
HOLD REGISTER 466 | 0-100% | READ | SAF Position | [0, 100]
HOLD REGISTER 467 | 0-100% | WRITE | SAF Minimum Referance | [0, 100]
HOLD REGISTER 468 | m3/h | READ | SAF Air Flow Fan 1 | [0, 65536]
HOLD REGISTER 469 | m3/h | READ | SAF Air Flow Fan 2 | [0, 65536]
HOLD REGISTER 470 | m3/h | READ | SAF Air Flow | [0, 65536]
HOLD REGISTER 471 | s | WRITE | SAF Start Delay | [0, 250]
HOLD REGISTER 472 | s | WRITE | SAF Stop Delay | [0, 250]
HOLD REGISTER 473 | s | READ | SAF Delayed Stop Position | [0, 100]
HOLD REGISTER 474 | s | READ | SAF Delayed Start Position | [0, 100]
HOLD REGISTER 475 | Pa | WRITE | SAF Pressure High Alarm Set | [0, 10000]
HOLD REGISTER 476 | Pa | READ | SAF Duct Press | [0, 65536]
HOLD REGISTER 477 | Pa | WRITE | SAF Duct Pressure BMS | [0, 7500]
HOLD REGISTER 478 | 0=m3/h , 1=Pa | WRITE | SAF Input Select Local | [0, 1]
HOLD REGISTER 479 | s | WRITE | SAF ITime | [5, 2000]
HOLD REGISTER 480 | s | WRITE | SAF PGain | [0.001, 100]
HOLD REGISTER 481 | s | WRITE | SAF ITimePre | [5, 2000]
HOLD REGISTER 482 | s | WRITE | SAF PGainPre | [0.001, 100]
HOLD REGISTER 151 | 0=Normal, 1=Alarm | READ | SAF Pressure High Alarm | [0, 1]
HOLD REGISTER 93 | 0=Normal, 1=Alarm | READ | SAF Pressure Sensor Comm Alarm | [0, 1]
HOLD REGISTER 100 | 0=Normal, 1=Alarm | READ | SAF Low Air Flow Alarm | [0, 1]
HOLD REGISTER 495 | 0-100% | WRITE | EAF Manuel Referance BMS | [0, 100]
HOLD REGISTER 496 | 0-100% | READ | EAF Actual Manuel Referance | [0, 100]
HOLD REGISTER 497 | 0=ManuelStop, 1=Maneul, 2=Auto | WRITE | EAF Mode Select BMS | [0, 2]
HOLD REGISTER 498 | 0=ManuelStop, 1=Maneul, 2=Auto | READ | EAF Actual Mode | [0, 2]
HOLD REGISTER 499 | m3/h | WRITE | EAF Air Volume Set BMS | [0, 60000]
HOLD REGISTER 500 | m3/h | READ | EAF Actual Air Vol Set | [0, 40000]
HOLD REGISTER 501 | 0-100% | READ | EAF Position | [0, 100]
HOLD REGISTER 502 | 0-100% | WRITE | EAF Minimum Referance | [0, 100]
HOLD REGISTER 503 | m3/h | READ | EAF Air Flow Fan 1 | [0, 65536]
HOLD REGISTER 504 | m3/h | READ | EAF Air Flow Fan 2 | [0, 65536]
HOLD REGISTER 505 | m3/h | READ | EAF Air Flow | [0, 65536]
HOLD REGISTER 506 | s | WRITE | EAF Start Delay | [0, 250]
HOLD REGISTER 507 | s | WRITE | EAF Stop Delay | [0, 250]
HOLD REGISTER 508 | s | READ | EAF Delayed Stop Position | [0, 100]
HOLD REGISTER 509 | s | READ | EAF Delayed Start Position | [0, 100]
HOLD REGISTER 510 | Pa | WRITE | EAF Pressure High Alarm Set | [0, 10000]
HOLD REGISTER 511 | Pa | READ | EAF Duct Press | [0, 65536]
HOLD REGISTER 512 | Pa | WRITE | EAF Duct Pressure BMS | [0, 7500]
HOLD REGISTER 513 | 0=m3/h , 1=Pa | WRITE | EAF Input Select Local | [0, 1]
HOLD REGISTER 514 | s | WRITE | EAF ITime | [5, 2000]
HOLD REGISTER 515 | s | WRITE | EAF PGain | [0.001, 100]
HOLD REGISTER 516 | s | WRITE | EAF ITimePre | [5, 2000]
HOLD REGISTER 517 | s | WRITE | EAF PGainPre | [0.001, 100]
HOLD REGISTER 153 | 0=Normal, 1=Alarm | READ | EAF Pressure High Alarm | [0, 1]
HOLD REGISTER 94 | 0=Normal, 1=Alarm | READ | EAF Pressure Sensor Comm Alarm | [0, 1]
HOLD REGISTER 101 | 0=Normal, 1=Alarm | READ | EAF Low Air Flow Alarm | [0, 1]
HOLD REGISTER 518 | 0=Stopped, 1=Running | READ | Humidifier 1 Start | [0, 1]
HOLD REGISTER 527 | 0=Stopped, 1=Running | READ | Humidifier 1 Run Status | [0, 1]
HOLD REGISTER 538 | 0-100% | WRITE | Humidifier 1 Manuel Position BMS | [0, 100]
HOLD REGISTER 539 | 0=ManuelStop, 1=Maneul, 2=Auto | WRITE | Humidifier 1 Mode Select BMS | [0, 2]
HOLD REGISTER 178 | 0=Normal, 1=Alarm | READ | Humidifier Alarm 1 | [0, 1]
HOLD REGISTER 519 | 0=Stopped, 1=Running | READ | Humidifier 2 Start | [0, 1]
HOLD REGISTER 528 | 0=Stopped, 1=Running | READ | Humidifier 2 Run Status | [0, 1]
HOLD REGISTER 540 | 0-100% | WRITE | Humidifier 2 Manuel Position BMS | [0, 100]
HOLD REGISTER 541 | 0=ManuelStop, 1=Maneul, 2=Auto | WRITE | Humidifier 2 Mode Select BMS | [0, 2]
HOLD REGISTER 179 | 0=Normal, 1=Alarm | READ | Humidifier Alarm 2 | [0, 1]
HOLD REGISTER 520 | 0=Stopped, 1=Running | READ | Humidifier 3 Start | [0, 1]
HOLD REGISTER 529 | 0=Stopped, 1=Running | READ | Humidifier 3 Run Status | [0, 1]
HOLD REGISTER 542 | 0-100% | WRITE | Humidifier 3 Manuel Position BMS | [0, 100]
HOLD REGISTER 543 | 0=ManuelStop, 1=Maneul, 2=Auto | WRITE | Humidifier 3 Mode Select BMS | [0, 2]
HOLD REGISTER 180 | 0=Normal, 1=Alarm | READ | Humidifier Alarm 3 | [0, 1]
HOLD REGISTER 521 | 0=Stopped, 1=Running | READ | Humidifier 4 Start | [0, 1]
HOLD REGISTER 530 | 0=Stopped, 1=Running | READ | Humidifier 4 Run Status | [0, 1]
HOLD REGISTER 544 | 0-100% | WRITE | Humidifier 4 Manuel Position BMS | [0, 100]
HOLD REGISTER 545 | 0=ManuelStop, 1=Maneul, 2=Auto | WRITE | Humidifier 4 Mode Select BMS | [0, 2]
HOLD REGISTER 181 | 0=Normal, 1=Alarm | READ | Humidifier Alarm 4 | [0, 1]
HOLD REGISTER 522 | 0=Stopped, 1=Running | READ | Humidifier 5 Start | [0, 1]
HOLD REGISTER 531 | 0=Stopped, 1=Running | READ | Humidifier 5 Run Status | [0, 1]
HOLD REGISTER 546 | 0-100% | WRITE | Humidifier 5 Manuel Position BMS | [0, 100]
HOLD REGISTER 547 | 0=ManuelStop, 1=Maneul, 2=Auto | WRITE | Humidifier 5 Mode Select BMS | [0, 2]
HOLD REGISTER 182 | 0=Normal, 1=Alarm | READ | Humidifier Alarm 5 | [0, 1]
HOLD REGISTER 523 | 0=Stopped, 1=Running | READ | Humidifier 6 Start | [0, 1]
HOLD REGISTER 532 | 0=Stopped, 1=Running | READ | Humidifier 6 Run Status | [0, 1]
HOLD REGISTER 548 | 0-100% | WRITE | Humidifier 6 Manuel Position BMS | [0, 100]
HOLD REGISTER 549 | 0=ManuelStop, 1=Maneul, 2=Auto | WRITE | Humidifier 6 Mode Select BMS | [0, 2]
HOLD REGISTER 183 | 0=Normal, 1=Alarm | READ | Humidifier Alarm 6 | [0, 1]
HOLD REGISTER 524 | 0=Stopped, 1=Running | READ | Humidifier 7 Start | [0, 1]
HOLD REGISTER 533 | 0=Stopped, 1=Running | READ | Humidifier 7 Run Status | [0, 1]
HOLD REGISTER 550 | 0-100% | WRITE | Humidifier 7 Manuel Position BMS | [0, 100]
HOLD REGISTER 551 | 0=ManuelStop, 1=Maneul, 2=Auto | WRITE | Humidifier 7 Mode Select BMS | [0, 2]
HOLD REGISTER 184 | 0=Normal, 1=Alarm | READ | Humidifier Alarm 7 | [0, 1]
HOLD REGISTER 525 | 0=Stopped, 1=Running | READ | Humidifier 8 Start | [0, 1]
HOLD REGISTER 534 | 0=Stopped, 1=Running | READ | Humidifier 8 Run Status | [0, 1]
HOLD REGISTER 552 | 0-100% | WRITE | Humidifier 8 Manuel Position BMS | [0, 100]
HOLD REGISTER 553 | 0=ManuelStop, 1=Maneul, 2=Auto | WRITE | Humidifier 8 Mode Select BMS | [0, 2]
HOLD REGISTER 185 | 0=Normal, 1=Alarm | READ | Humidifier Alarm 8 | [0, 1]
HOLD REGISTER 554 | 0-8 | WRITE | Humidifier Capacity | [0, 8]
HOLD REGISTER 555 | C | READ | Humidifier Saturated Temp | [-64, 64]
HOLD REGISTER 556 | g/kg | READ | Humidifier Calculated Hum Set | [-64, 64]
HOLD REGISTER 557 | 0-100% | WRITE | Hum Set BMS | [4, 20]
HOLD REGISTER 558 | 0-100% | WRITE | Supply Hum Max BMS | [4, 20]
HOLD REGISTER 559 | 0-100% | WRITE | Supply Hum Min BMS | [4, 20]
HOLD REGISTER 560 | 0-5 | WRITE | Deadband Hum Set BMS | [0, 5]
HOLD REGISTER 561 | 0=Supply, 1=Return | WRITE | Hum Control Type Select BMS | [0, 1]
HOLD REGISTER 562 | 0=Off, 1=On | READ | Humectation ON | [0, 1]
HOLD REGISTER 563 | 0=Off, 1=On | READ | Dehumectation ON | [0, 1]
HOLD REGISTER 564 | g/kg | READ | Hum Set ABS | [-64, 64]
HOLD REGISTER 571 | g/kg | READ | Humidifier Room ABS | [-64, 64]
HOLD REGISTER 572 | 0=Off, 1=On | WRITE | Humidifier Room Hum Sel | [0, 1]
HOLD REGISTER 573 | C | READ | Humidifier WetBulp Temp | [-64, 64]
HOLD REGISTER 575 | 0=Off, 1=Auto, 2=Heat, 3=Cool | WRITE | ChangeOver Valve Control Select | [0, 3]
HOLD REGISTER 576 | 0=Off, 1=Manuel, 2=Auto | WRITE | ChangeOver Valve Mode Sel | [0, 2]
HOLD REGISTER 577 | 0-100% | WRITE | ChangeOver Valve Manuel Referance | [0, 100]
HOLD REGISTER 578 | C | WRITE | ChangeOver Valve Control Temp Value | [-64, 64]
HOLD REGISTER 579 | 0-100% | READ | ChangeOver Valve Feedback | [0, 100]
HOLD REGISTER 580 | 0-100% | READ | ChangeOver Valve Position | [0, 100]
HOLD REGISTER 581 | 0=Off, 1=Auto, 2=Heat, 3=Cool | WRITE | ChangeOver Valve Control Select BMS | [0, 3]
HOLD REGISTER 582 | 0=Off, 1=Manuel, 2=Auto | WRITE | ChangeOver Valve Mode Select BMS | [0, 2]
HOLD REGISTER 583 | 0-100% | WRITE | ChangeOver Valve Manuel Referance BMS | [0, 100]
HOLD REGISTER 584 | 0=Off, 1=On | READ | ChangeOver Valve Active | [0, 1]
HOLD REGISTER 585 | 0=Off, 1=Heat, 2=Cool | READ | ChangeOver Valve Mode | [0, 2]

## BACnetRegister
BACnet NAME | UNIT | ACTION | DESCRIPTION | INTERVAL
SupplyAirSensorMB\TmpVal | C | READ | Supply Air Sensor Temp Value | [-100, 100]
SupplyAirSensorMB\HumVal | %rH | READ | Supply Air Sensor Hum Value | [0, 100]
SupplyAirSensorMB\CO2Val | ppm | READ | Supply Air Sensor CO2 Value | [0, 2000]
SupplyAirSensorMB\EntVal | kJ/kg | READ | Supply Air Sensor Entropy Value | [0, 2000]
SupplyAirSensorMB\AbsHum | g/kg | READ | Supply Air Sensor ABS Hum Value | [0, 2000]
SupplyAirSensorMB\SupplyAirSensorMB.CommAlarm | 0=Normal, 1=Alarm | READ | Supply Air Sensor Comm Alarm | [0, 1]
ReturnAirSensorMB\TmpVal | C | READ | Return Air Sensor Temp Value | [-100, 100]
ReturnAirSensorMB\HumVal | %rH | READ | Return Air Sensor Hum Value | [0, 100]
ReturnAirSensorMB\CO2Val | ppm | READ | Return Air Sensor CO2 Value | [0, 2000]
ReturnAirSensorMB\EntVal | kJ/kg | READ | Return Air Sensor Entropy Value | [0, 2000]
ReturnAirSensorMB\AbsHum | g/kg | READ | Return Air Sensor ABS Hum Value | [0, 2000]
ReturnAirSensorMB\ReturnAirSensorMB.CommAlarm | 0=Normal, 1=Alarm | READ | Return Air Sensor Comm Alarm | [0, 1]
FreshAirSensorMB\TmpVal | c | READ | Fresh Air Sensor Temp Value | [-100, 100]
FreshAirSensorMB\HumVal | %rH | READ | Fresh Air Sensor Hum Value | [0, 100]
FreshAirSensorMB\CO2Val | ppm | READ | Fresh Air Sensor CO2 Value | [0, 2000]
FreshAirSensorMB\EntVal | kJ/kg | READ | Fresh Air Sensor Entropy Value | [0, 2000]
FreshAirSensorMB\AbsHum | g/kg | READ | Fresh Air Sensor ABS Hum Value | [0, 2000]
FreshAirSensorMB\FreshAirSensorMB.CommAlarm | 0=Normal, 1=Alarm | READ | Fresh Air Sensor Comm Alarm | [0, 1]
AfterCoilAirSensorMB\TmpVal | C | READ | AfterCoil Air Sensor Temp Value | [-100, 100]
AfterCoilAirSensorMB\HumVal | %rH | READ | AfterCoil Air Sensor Hum Value | [0, 100]
AfterCoilAirSensorMB\CO2Val | ppm | READ | AfterCoil Air Sensor CO2 Value | [0, 2000]
AfterCoilAirSensorMB\AfterCoilAirSensorMB.CommAlarm | 0=Normal, 1=Alarm | READ | After Coil Air Sensor Comm Alarm | [0, 1]
ExhaustAirSensorMB\TmpVal | C | READ | Exhaust Air Sensor Temp Value | [-100, 100]
ExhaustAirSensorMB\HumVal | %rH | READ | Exhaust Air Sensor Hum Value | [0, 100]
ExhaustAirSensorMB\CO2Val | ppm | READ | Exhaust Air Sensor CO2 Value | [0, 2000]
ExhaustAirSensorMB\ExhaustAirSensorMB.CommAlarm | 0=Normal, 1=Alarm | READ | Exhaust Air Sensor Comm Alarm | [0, 1]
Return Co2\CO2Value | ppm | READ | Return CO2 Sensor CO2 Value | [0, 2000]
Room Temp\Room Temp | C | READ | Room Sensor Temp Value | [-100, 100]
Room Hum\Room Hum | %rH | READ | Room Sensor Hum Value | [0, 100]
Water Temp\Water Temp | C | READ | Water Sensor Temp Value | [-100, 100]
Room Temp1\Room Temp | C | READ | Room Sensor 2 Temp Value | [-100, 100]
MixingAirSensorMB\TmpVal | C | READ | Mix Air Sensor Temp Value | [-100, 100]
MixingAirSensorMB\HumVal | % | READ | Mix Air Sensor Hum Value | [0, 100]
MixingAirSensorMB\CO2Val | PPM | READ | Mix Air Sensor CO2 Value | [0, 2000]
MixingAirSensorMB\MixingAirSensorMB.CommAlarm | 0=Normal, 1=Alarm | READ | Mix Air Sensor Comm Alarm | [0, 1]
ReturnCO2AirSensorMB\TmpVal | C | READ | Return CO2 Air Sensor Temp Value | [-100, 100]
ReturnCO2AirSensorMB\CO2Val | PPM | READ | Return CO2 Air Sensor CO2 Value | [0, 2000]
ReturnCO2AirSensorMB\ReturnCO2AirSensorMB.CommAlarm | 0=Normal, 1=Alarm | READ | Return CO2 Air Sensor Comm Alarm | [0, 1]
TempAVG\Room1En | 0=Off, 1=On | WRITE | Temp Average Room Sensor 1 EN | [0, 1]
TempAVG\Room2En | 0=Off, 1=On | WRITE | Temp Average Room Sensor 2 EN | [0, 1]
TempAVG\Room3En | 0=Off, 1=On | WRITE | Temp Average Room Sensor 3 EN | [0, 1]
TempAVG\Room4En | 0=Off, 1=On | WRITE | Temp Average Room Sensor 4 EN | [0, 1]
TempAVG\Room_TempAVG | C | READ | Temp Average Temp Average | [-64, 64]
BmsTemp_Hum\RoomTempFromBms | C | WRITE | Room Temp From Bms | [-64, 64]
BmsTemp_Hum\RoomHumFromBms | % | WRITE | Room Hum From Bms | [0, 100]
BmsTemp_Hum\FreshTempFromBms | C | WRITE | Fresh Temp From Bms | [-64, 64]
EBMFanCont\SAF Ebm RPM | rpm | READ | SAF EBM 1 RPM | [0, 1000]
EBMFanCont\SAF Ebm Power | kW | READ | SAF EBM 1 Power | [0, 100000]
EBMFanCont\SAF Ebm Current | A | READ | SAF EBM 1 Current | [-64, 64]
EBMFanCont\SAF EBM Motor Tmp. | C | READ | SAF EBM 1 Motor Temp | [-1000, 1000]
EBMFanCont\SAF EBM Motor Run Hour | h | READ | SAF EBM 1 Motor Run Hour | [0, 10000000]
EBMFanCont\EBMFanCont.MotorAlarm | 0=Normal, 1=Alarm | READ | SAF EBM 1 Motor Alarm | [0, 1]
EBMFanCont\EBMFanCont.CommAlarm | 0=Normal, 1=Alarm | READ | SAF EBM 1 Comm Alarm | [0, 1]
EBMFanCont\EBMFanCont.MotorWarning | 0=Normal, 1=Alarm | READ | SAF EBM 1 Motor Warning | [0, 1]
EBMFanCont1\SAF Ebm RPM | rpm | READ | SAF EBM 2 RPM | [0, 1000]
EBMFanCont1\SAF Ebm Power | kW | READ | SAF EBM 2 Power | [0, 100000]
EBMFanCont1\SAF Ebm Current | A | READ | SAF EBM 2 Current | [-64, 64]
EBMFanCont1\SAF EBM Motor Tmp. | C | READ | SAF EBM 2 Motor Temp | [-1000, 1000]
EBMFanCont1\SAF EBM Motor Run Hour | h | READ | SAF EBM 2 Motor Run Hour | [0, 10000000]
EBMFanCont1\EBMFanCont1.MotorAlarm | 0=Normal, 1=Alarm | READ | SAF EBM 2 Motor Alarm | [0, 1]
EBMFanCont1\EBMFanCont1.CommAlarm | 0=Normal, 1=Alarm | READ | SAF EBM 2 Comm Alarm | [0, 1]
EBMFanCont1\EBMFanCont1.MotorWarning | 0=Normal, 1=Alarm | READ | SAF EBM 2 Motor Warning | [0, 1]
EBMFanCont2\SAF Ebm RPM | rpm | READ | SAF EBM 3 RPM | [0, 1000]
EBMFanCont2\SAF Ebm Power | kW | READ | SAF EBM 3 Power | [0, 100000]
EBMFanCont2\SAF Ebm Current | A | READ | SAF EBM 3 Current | [-64, 64]
EBMFanCont2\SAF EBM Motor Tmp. | C | READ | SAF EBM 3 Motor Temp | [-1000, 1000]
EBMFanCont2\SAF EBM Motor Run Hour | h | READ | SAF EBM 3 Motor Run Hour | [0, 10000000]
EBMFanCont2\EBMFanCont2.MotorAlarm | 0=Normal, 1=Alarm | READ | SAF EBM 3 Motor Alarm | [0, 1]
EBMFanCont2\EBMFanCont2.CommAlarm | 0=Normal, 1=Alarm | READ | SAF EBM 3 Comm Alarm | [0, 1]
EBMFanCont2\EBMFanCont2.MotorWarning | 0=Normal, 1=Alarm | READ | SAF EBM 3 Motor Warning | [0, 1]
EBMFaneExCont\EAF Ebm RPM | rpm | READ | EAF EBM 1 RPM | [0, 1000]
EBMFaneExCont\EAF Ebm Power | kW | READ | EAF EBM 1 Power | [0, 100000]
EBMFaneExCont\EAF Ebm Current | A | READ | EAF EBM 1 Current | [-64, 64]
EBMFaneExCont\EAF EBM Motor Tmp. | C | READ | EAF EBM 1 Motor Temp | [-1000, 1000]
EBMFaneExCont\EAF EBM Motor Run Hour | h | READ | EAF EBM 1 Motor Run Hour | [0, 10000000]
EBMFaneExCont\EBMFaneExCont.MotorAlarm | 0=Normal, 1=Alarm | READ | EAF EBM 1 Motor Alarm | [0, 1]
EBMFaneExCont\EBMFaneExCont.CommAlarm | 0=Normal, 1=Alarm | READ | EAF EBM 1 Comm Alarm | [0, 1]
EBMFaneExCont\EBMFaneExCont.MotorWarning | 0=Normal, 1=Alarm | READ | EAF EBM 1 Motor Warning | [0, 1]
EBMFaneExCont1\EAF Ebm RPM | rpm | READ | EAF EBM 2 RPM | [0, 1000]
EBMFaneExCont1\EAF Ebm Power | kW | READ | EAF EBM 2 Power | [0, 100000]
EBMFaneExCont1\EAF Ebm Current | A | READ | EAF EBM 2 Current | [-64, 64]
EBMFaneExCont1\EAF EBM Motor Tmp. | C | READ | EAF EBM 2 Motor Temp | [-1000, 1000]
EBMFaneExCont1\EAF EBM Motor Run Hour | h | READ | EAF EBM 2 Motor Run Hour | [0, 10000000]
EBMFaneExCont1\EBMFaneExCont1.MotorAlarm | 0=Normal, 1=Alarm | READ | EAF EBM 2 Motor Alarm | [0, 1]
EBMFaneExCont1\EBMFaneExCont1.CommAlarm | 0=Normal, 1=Alarm | READ | EAF EBM 2 Comm Alarm | [0, 1]
EBMFaneExCont1\EBMFaneExCont1.MotorWarning | 0=Normal, 1=Alarm | READ | EAF EBM 2 Motor Warning | [0, 1]
EBMFaneExCont2\EAF Ebm RPM | rpm | READ | EAF EBM 3 RPM | [0, 1000]
EBMFaneExCont2\EAF Ebm Power | kW | READ | EAF EBM 3 Power | [0, 100000]
EBMFaneExCont2\EAF Ebm Current | A | READ | EAF EBM 3 Current | [-64, 64]
EBMFaneExCont2\EAF EBM Motor Tmp. | C | READ | EAF EBM 3 Motor Temp | [-1000, 1000]
EBMFaneExCont2\EAF EBM Motor Run Hour | h | READ | EAF EBM 3 Motor Run Hour | [0, 10000000]
EBMFaneExCont2\EBMFaneExCont2.MotorAlarm | 0=Normal, 1=Alarm | READ | EAF EBM 3 Motor Alarm | [0, 1]
EBMFaneExCont2\EBMFaneExCont2.CommAlarm | 0=Normal, 1=Alarm | READ | EAF EBM 3 Comm Alarm | [0, 1]
EBMFaneExCont2\EBMFaneExCont2.MotorWarning | 0=Normal, 1=Alarm | READ | EAF EBM 3 Motor Warning | [0, 1]
ZiehlAbeggSup\ZiehlAbeggSup.RPM | rpm | READ | ZiehlAbegg Supply 1 RPM | [0, 100000]
ZiehlAbeggSup\ZiehlAbeggSup.Power | kW | READ | ZiehlAbegg Supply 1 Power | [0, 100000]
ZiehlAbeggSup\ZiehlAbeggSup.Current | A | READ | ZiehlAbegg Supply 1 Current | [0, 100000]
ZiehlAbeggSup\ZiehlAbeggSup.CommAlarm | 0=Normal, 1=Alarm | READ | ZiehlAbegg Supply 1 Comm Alarm | [0, 1]
ZiehlAbeggSup\ZiehlAbeggSup.Alarm | 0=Normal, 1=Alarm | READ | ZiehlAbegg Supply 1 Alarm | [0, 1]
ZiehlAbeggExh\ZiehlAbeggExh.RPM | rpm | READ | ZiehlAbegg Exhaust 1 RPM | [0, 100000]
ZiehlAbeggExh\ZiehlAbeggExh.Power | kW | READ | ZiehlAbegg Exhaust 1 Power | [0, 100000]
ZiehlAbeggExh\ZiehlAbeggExh.Current | A | READ | ZiehlAbegg Exhaust 1 Current | [0, 100000]
ZiehlAbeggExh\ZiehlAbeggExh.CommAlarm | 0=Normal, 1=Alarm | READ | ZiehlAbegg Exhaust 1 Comm Alarm | [0, 1]
ZiehlAbeggExh\ZiehlAbeggExh.Alarm | 0=Normal, 1=Alarm | READ | ZiehlAbegg Exhaust 1 Alarm | [0, 1]
ZiehlAbeggSup1\ZiehlAbeggSup1.RPM | rpm | READ | ZiehlAbegg Supply 2 RPM | [0, 100000]
ZiehlAbeggSup1\ZiehlAbeggSup1.Power | kW | READ | ZiehlAbegg Supply 2 Power | [0, 100000]
ZiehlAbeggSup1\ZiehlAbeggSup1.Current | A | READ | ZiehlAbegg Supply 2 Current | [0, 100000]
ZiehlAbeggSup1\ZiehlAbeggSup1.CommAlarm | 0=Normal, 1=Alarm | READ | ZiehlAbegg Supply 2 Comm Alarm | [0, 1]
ZiehlAbeggSup1\ZiehlAbeggSup1.Alarm | 0=Normal, 1=Alarm | READ | ZiehlAbegg Supply 2 Alarm | [0, 1]
ZiehlAbeggExh1\ZiehlAbeggExh1.RPM | rpm | READ | ZiehlAbegg Exhaust 2 RPM | [0, 100000]
ZiehlAbeggExh1\ZiehlAbeggExh1.Power | kW | READ | ZiehlAbegg Exhaust 2 Power | [0, 100000]
ZiehlAbeggExh1\ZiehlAbeggExh1.Current | A | READ | ZiehlAbegg Exhaust 2 Current | [0, 100000]
ZiehlAbeggExh1\ZiehlAbeggExh1.CommAlarm | 0=Normal, 1=Alarm | READ | ZiehlAbegg Exhaust 2 Comm Alarm | [0, 1]
ZiehlAbeggExh1\ZiehlAbeggExh1.Alarm | 0=Normal, 1=Alarm | READ | ZiehlAbegg Exhaust 2 Alarm | [0, 1]
ZiehlAbeggSup1\ZiehlAbeggSup2.RPM | rpm | READ | ZiehlAbegg Supply 3 RPM | [0, 100000]
ZiehlAbeggSup1\ZiehlAbeggSup2.Power | kW | READ | ZiehlAbegg Supply 3 Power | [0, 100000]
ZiehlAbeggSup1\ZiehlAbeggSup2.Current | A | READ | ZiehlAbegg Supply 3 Current | [0, 100000]
ZiehlAbeggSup2\ZiehlAbeggSup2.CommAlarm | 0=Normal, 1=Alarm | READ | ZiehlAbegg Supply 3 Comm Alarm | [0, 1]
ZiehlAbeggSup2\ZiehlAbeggSup2.Alarm | 0=Normal, 1=Alarm | READ | ZiehlAbegg Supply 3 Alarm | [0, 1]
ZiehlAbeggExh1\ZiehlAbeggExh2.RPM | rpm | READ | ZiehlAbegg Exhaust 3 RPM | [0, 100000]
ZiehlAbeggExh1\ZiehlAbeggExh2.Power | kW | READ | ZiehlAbegg Exhaust 3 Power | [0, 100000]
ZiehlAbeggExh1\ZiehlAbeggExh2.Current | A | READ | ZiehlAbegg Exhaust 3 Current | [0, 100000]
ZiehlAbeggExh2\ZiehlAbeggExh2.CommAlarm | 0=Normal, 1=Alarm | READ | ZiehlAbegg Exhaust 3 Comm Alarm | [0, 1]
ZiehlAbeggExh2\ZiehlAbeggExh2.Alarm | 0=Normal, 1=Alarm | READ | ZiehlAbegg Exhaust 3 Alarm | [0, 1]
FC101Vant1\FCRunning | 0=Stopped, 1=Running | READ | FC101Vant1 FCRunning | [0, 1]
FC101Vant1\FCReady | 0=Busy, 1=Ready | READ | FC101Vant1 FCReady | [0, 1]
FC101Vant1\CurrentVal | A | READ | FC101Vant1 Current Valve | [0, 100000]
FC101Vant1\HertzVal | Hz | READ | FC101Vant1 Hertz Valve | [0, 100000]
FC101Vant1\RPMVal | rpm | READ | FC101Vant1 RPM Valve | [0, 100000]
FC101Vant1\kWVal | kW | READ | FC101Vant1 kW Valve | [0, 100000]
FC101Vant1\VoltVal | V | READ | FC101Vant1 Volt Valve | [0, 100000]
FC101Vant1\TorqueVal | t | READ | FC101Vant1 Torque Valve | [0, 100000]
FC101Vant1\MinRef | Hz | READ | FC101Vant1 Min Referance | [0, 100000]
FC101Vant1\MaxRef | Hz | READ | FC101Vant1 Max Referance | [0, 100000]
FC101Vant1\RunningHour | h | READ | FC101Vant1 Running Hour | [0, 100000]
FC101Vant1\OperationHour | h | READ | FC101Vant1 Operation Hour | [0, 100000]
FC101Vant1\kWhCounter |  | READ | FC101Vant1 kWh Counter | [0, 100000]
FC101Vant1\FCAutoMode | 0=HandOn,1=Auto | READ | FC101Vant1 FCAuto Mode | [0, 1]
FC101Vant1\ControlReady | 0=NotReady,1=Ready | READ | FC101Vant1 Control Ready | [0, 1]
FC101Vant1\FC101Vant1.CommAlarm | 0=Normal, 1=Alarm | READ | FC101Vant 1 Comm Alarm | [0, 1]
FC101Vant1\FC101Vant1.FcAlarm | 0=Normal, 1=Alarm | READ | FC101Vant 1 FCAlarm | [0, 1]
FC101Vant2\FCRunning | 0=Off, 1=On | READ | FC101Vant2 FCRunning | [0, 1]
FC101Vant2\FCReady | 0=Off, 1=On | READ | FC101Vant2 FCReady | [0, 1]
FC101Vant2\CurrentVal | A | READ | FC101Vant2 Current Valve | [0, 100000]
FC101Vant2\HertzVal | Hz | READ | FC101Vant2 Hertz Valve | [0, 100000]
FC101Vant2\RPMVal | rpm | READ | FC101Vant2 RPM Valve | [0, 100000]
FC101Vant2\kWVal | kW | READ | FC101Vant2 kW Valve | [0, 100000]
FC101Vant2\VoltVal | V | READ | FC101Vant2 Volt Valve | [0, 100000]
FC101Vant2\TorqueVal | t | READ | FC101Vant2 Torque Valve | [0, 100000]
FC101Vant2\MinRef | Hz | READ | FC101Vant2 Min Referance | [0, 100000]
FC101Vant2\MaxRef | Hz | READ | FC101Vant2 Max Referance | [0, 100000]
FC101Vant2\RunningHour | h | READ | FC101Vant2 Running Hour | [0, 100000]
FC101Vant2\OperationHour | h | READ | FC101Vant2 Operation Hour | [0, 100000]
FC101Vant2\kWhCounter |  | READ | FC101Vant2 kWh Counter | [0, 100000]
FC101Vant2\FCAutoMode | 0=HandOn,1=Auto | READ | FC101Vant2 FCAuto Mode | [0, 1]
FC101Vant2\ControlReady | 0=NotReady,1=Ready | READ | FC101Vant2 Control Ready | [0, 1]
FC101Vant2\FC101Vant2.CommAlarm | 0=Normal, 1=Alarm | READ | FC101Vant 2 Comm Alarm | [0, 1]
FC101Vant2\FC101Vant2.FcAlarm | 0=Normal, 1=Alarm | READ | FC101Vant 2 FCAlarm | [0, 1]
FC101Asp1\FCRunning | 0=Off, 1=On | READ | FC101Asp1 FCRunning | [0, 1]
FC101Asp1\FCReady | 0=Off, 1=On | READ | FC101Asp1 FCReady | [0, 1]
FC101Asp1\CurrentVal | A | READ | FC101Asp1 Current Valve | [0, 100000]
FC101Asp1\HertzVal | Hz | READ | FC101Asp1 Hertz Valve | [0, 100000]
FC101Asp1\RPMVal | rpm | READ | FC101Asp1 RPM Valve | [0, 100000]
FC101Asp1\kWVal | kW | READ | FC101Asp1 kW Valve | [0, 100000]
FC101Asp1\VoltVal | V | READ | FC101Asp1 Volt Valve | [0, 100000]
FC101Asp1\TorqueVal | t | READ | FC101Asp1 Torque Valve | [0, 100000]
FC101Asp1\MinRef | Hz | READ | FC101Asp1 Min Referance | [0, 100000]
FC101Asp1\MaxRef | Hz | READ | FC101Asp1 Max Referance | [0, 100000]
FC101Asp1\RunningHour | h | READ | FC101Asp1 Running Hour | [0, 100000]
FC101Asp1\OperationHour | h | READ | FC101Asp1 Operation Hour | [0, 100000]
FC101Asp1\kWhCounter |  | READ | FC101Asp1 kWh Counter | [0, 100000]
FC101Asp1\FCAutoMode | 0=HandOn,1=Auto | READ | FC101Asp1 FCAuto Mode | [0, 1]
FC101Asp1\ControlReady | 0=NotReady,1=Ready | READ | FC101Asp1 Control Ready | [0, 1]
FC101Asp1\FC101Asp1.CommAlarm | 0=Normal, 1=Alarm | READ | FC101Asp 1 Comm Alarm | [0, 1]
FC101Asp1\FC101Asp1.FcAlarm | 0=Normal, 1=Alarm | READ | FC101Asp 1 FCAlarm | [0, 1]
FC101Asp2\FCRunning | 0=Off, 1=On | READ | FC101Asp2 FCRunning | [0, 1]
FC101Asp2\FCReady | 0=Off, 1=On | READ | FC101Asp2 FCReady | [0, 1]
FC101Asp2\CurrentVal | A | READ | FC101Asp2 Current Valve | [0, 100000]
FC101Asp2\HertzVal | Hz | READ | FC101Asp2 Hertz Valve | [0, 100000]
FC101Asp2\RPMVal | rpm | READ | FC101Asp2 RPM Valve | [0, 100000]
FC101Asp2\kWVal | kW | READ | FC101Asp2 kW Valve | [0, 100000]
FC101Asp2\VoltVal | V | READ | FC101Asp2 Volt Valve | [0, 100000]
FC101Asp2\TorqueVal | t | READ | FC101Asp2 Torque Valve | [0, 100000]
FC101Asp2\MinRef | Hz | READ | FC101Asp2 Min Referance | [0, 100000]
FC101Asp2\MaxRef | Hz | READ | FC101Asp2 Max Referance | [0, 100000]
FC101Asp2\RunningHour | h | READ | FC101Asp2 Running Hour | [0, 100000]
FC101Asp2\OperationHour | h | READ | FC101Asp2 Operation Hour | [0, 100000]
FC101Asp2\kWhCounter |  | READ | FC101Asp2 kWh Counter | [0, 100000]
FC101Asp2\FCAutoMode | 0=HandOn,1=Auto | READ | FC101Asp2 FCAuto Mode | [0, 1]
FC101Asp2\ControlReady | 0=NotReady,1=Ready | READ | FC101Asp2 Control Ready | [0, 1]
FC101Asp2\FC101Asp2.CommAlarm | 0=Normal, 1=Alarm | READ | FC101Asp 2 Comm Alarm | [0, 1]
FC101Asp2\FC101Asp2.FcAlarm | 0=Normal, 1=Alarm | READ | FC101Asp 2 FCAlarm | [0, 1]
DXControl\DXControl.Dx1Alarm | 0=Normal, 1=Alarm | READ | DX Alarm 1 | [0, 1]
DXControl\DXControl.DX1Defrost | 0=Normal, 1=Alarm | READ | DX Defrost 1 | [0, 1]
DXControl\DXControl.Dx2Alarm | 0=Normal, 1=Alarm | READ | DX Alarm 2 | [0, 1]
DXControl\DXControl.DX2Defrost | 0=Normal, 1=Alarm | READ | DX Defrost 2 | [0, 1]
DXControl\DXControl.Dx3Alarm | 0=Normal, 1=Alarm | READ | DX Alarm 3 | [0, 1]
DXControl\DXControl.DX3Defrost | 0=Normal, 1=Alarm | READ | DX Defrost 3 | [0, 1]
DXControl\DXControl.Dx4Alarm | 0=Normal, 1=Alarm | READ | DX Alarm 4 | [0, 1]
DXControl\DXControl.DX4Defrost | 0=Normal, 1=Alarm | READ | DX Defrost 4 | [0, 1]
DXControl\DXControl.Dx5Alarm | 0=Normal, 1=Alarm | READ | DX Alarm 5 | [0, 1]
DXControl\DXControl.DX5Defrost | 0=Normal, 1=Alarm | READ | DX Defrost 5 | [0, 1]
DXControl\CapValuee | 0-100% | READ | DX Capacity Value | [-64, 64]
DXControl\DX_Status1 | 0=Off, 1=On | READ | DX Status | [0, 1]
DXControl\DX_mode | 0=Off, 1=Cool, 2=Heat, 3=Dehum | READ | DX Mode | [0, 3]
Alarm_Reset\Alarm_Reset | 0=Normal, 1=Alarm reset | WRITE | Alarm Reset | [0, 1]
Alarm\FreshF7FilterAlm | 0=Normal, 1=Alarm | READ | Fresh F7 Filter Alarm | [0, 1]
Alarm\FreshG4FilterAlm | 0=Normal, 1=Alarm | READ | Fresh G4 Filter Alarm | [0, 1]
Alarm\ReturnG4FilterAlm | 0=Normal, 1=Alarm | READ | Return G4 Filter Alarm | [0, 1]
Alarm\SupplyF9FilterAlm | 0=Normal, 1=Alarm | READ | Supply F9 Filter Alarm | [0, 1]
Alarm\FreshF9FilterAlm | 0=Normal, 1=Alarm | READ | Fresh F9 Filter Alarm | [0, 1]
Alarm\ReturnF7FilterAlm | 0=Normal, 1=Alarm | READ | Return F7 Filter Alarm | [0, 1]
Alarm\FreshM5FilterAlm | 0=Normal, 1=Alarm | READ | Fresh M5 Filter Alarm | [0, 1]
Alarm\FreshG2FilterAlm | 0=Normal, 1=Alarm | READ | Fresh G2 Filter Alarm | [0, 1]
Alarm\FreshF4FilterAlm | 0=Normal, 1=Alarm | READ | Fresh F4 Filter Alarm | [0, 1]
Alarm\ReturnM5FilterAlm | 0=Normal, 1=Alarm | READ | Return M5 Filter Alarm | [0, 1]
Alarm\ReturnF9FilterAlm | 0=Normal, 1=Alarm | READ | Return F9 Filter Alarm | [0, 1]
Alarm\ReturnG2FilterAlm | 0=Normal, 1=Alarm | READ | Return G2 Filter Alarm | [0, 1]
Alarm\SupplyM5FilterAlm | 0=Normal, 1=Alarm | READ | Supply M5 Filter Alarm | [0, 1]
Alarm\SupplyG4FilterAlm | 0=Normal, 1=Alarm | READ | Supply G4 Filter Alarm | [0, 1]
Alarm\SupplyF7FilterAlm | 0=Normal, 1=Alarm | READ | Supply F7 Filter Alarm | [0, 1]
Alarm\SupplyG2FilterAlm | 0=Normal, 1=Alarm | READ | Supply G2 Filter Alarm | [0, 1]
Alarm\HepaFilterAlm | 0=Normal, 1=Alarm | READ | Hepa Filter Alarm | [0, 1]
Alarm\H13FilterAlm | 0=Normal, 1=Alarm | READ | H13 Filter Alarm | [0, 1]
AHUStart\EMERGENCY | 0=Normal, 1=Alarm | READ | EMERGENCY | [0, 1]
AHUStart\FIREALARM | 0=Normal, 1=Alarm | READ | FIRE ALARM | [0, 1]
AHUStart\PHASEALARM | 0=Normal, 1=Alarm | READ | PHASE ALARM | [0, 1]
AHUStart\VANTDOORSW | 0=Normal, 1=Alarm | READ | VANT DOOR SW | [0, 1]
AHUStart\ASPDOORSW | 0=Normal, 1=Alarm | READ | ASP DOOR SW | [0, 1]
TmpControl\Frost Alarm | 0=Normal, 1=Alarm | READ | FROST ALARM | [0, 1]
ByPassDmpMB_Siemens\Dmp_Pos | 0-100% | READ | Bypass Damper Position | [0, 100]
BypassDmpCont\BypassModeSelLocal_BMS | 0=ManuelStop, 1=Maneul, 2=Auto | WRITE | Bypass Mode Select Local BMS | [0, 2]
BypassDmpCont\BypassManSetLocal_BMS | 0-100% | WRITE | Bypass Manuel Set Local BMS | [0, 100]
BypassDmpCont\BypassSetLocal_BMS | -5 25 C | WRITE | Bypass Set Local BMS | [-5, 25]
BypassDmpCont\BypassRecMod | 0=Off, 1=On | WRITE | Bypass Recover Mod | [0, 1]
ByPassDmpMB_Siemens\Dmp_Fdb | 0-100% | READ | Bypass Damper 1 Feedback | [0, 100]
ByPassDmpMB_Siemens\ByPassDmpMB_Siemens.CommAlarm | 0=Normal, 1=Alarm | READ | Bypass Damper 1 Comm Alarm | [0, 1]
ByPassDmpMB_Siemens\ByPassDmpMB_Siemens.FeedbackAlarm | 0=Normal, 1=Alarm | READ | Bypass Damper 1 Feedback Alarm | [0, 1]
ByPassDmpMB_Siemens\ByPassDmpMB_Siemens.Mechanical_fault | 0=Normal, 1=Alarm | READ | Bypass Damper 1 Mechanical Fault | [0, 1]
ByPassDmpMB_Siemens1\Dmp_Fdb | 0-100% | READ | Bypass Damper 2 Feedback | [0, 100]
ByPassDmpMB_Siemens1\ByPassDmpMB_Siemens1.CommAlarm | 0=Normal, 1=Alarm | READ | Bypass Damper 2 Comm Alarm | [0, 1]
ByPassDmpMB_Siemens1\ByPassDmpMB_Siemens1.FeedbackAlarm | 0=Normal, 1=Alarm | READ | Bypass Damper 2 Feedback Alarm | [0, 1]
ByPassDmpMB_Siemens1\ByPassDmpMB_Siemens1.Mechanical_fault | 0=Normal, 1=Alarm | READ | Bypass Damper 2 Mechanical Fault | [0, 1]
SupDmpMB_Siemens\Dmp_Pos | 0-100% | READ | Supply Damper Position | [0, 100]
SupDmpMB_Siemens\Dmp_Fdb | 0-100% | READ | Supply Damper 1 Feedback | [0, 100]
SupDmpMB_Siemens\SupDmpMB_Siemens.CommAlarm | 0=Normal, 1=Alarm | READ | Supply Damper 1 Comm Alarm | [0, 1]
SupDmpMB_Siemens\SupDmpMB_Siemens.FeedbackAlarm | 0=Normal, 1=Alarm | READ | Supply Damper 1 Feedback Alarm | [0, 1]
SupDmpMB_Siemens\SupDmpMB_Siemens.Mechanical_fault | 0=Normal, 1=Alarm | READ | Supply Damper 1 Mechanical Fault | [0, 1]
SupDmpMB_Siemens1\Dmp_Fdb | 0-100% | READ | Supply Damper 2 Feedback | [0, 100]
SupDmpMB_Siemens1\SupDmpMB_Siemens1.CommAlarm | 0=Normal, 1=Alarm | READ | Supply Damper 2 Comm Alarm | [0, 1]
SupDmpMB_Siemens1\SupDmpMB_Siemens1.FeedbackAlarm | 0=Normal, 1=Alarm | READ | Supply Damper 2 Feedback Alarm | [0, 1]
SupDmpMB_Siemens1\SupDmpMB_Siemens1.Mechanical_fault | 0=Normal, 1=Alarm | READ | Supply Damper 2 Mechanical Fault | [0, 1]
SupDmpMB_Siemens2\Dmp_Fdb | 0-100% | READ | Supply Damper 3 Feedback | [0, 100]
SupDmpMB_Siemens2\SupDmpMB_Siemens2.CommAlarm | 0=Normal, 1=Alarm | READ | Supply Damper 3 Comm Alarm | [0, 1]
SupDmpMB_Siemens2\SupDmpMB_Siemens2.FeedbackAlarm | 0=Normal, 1=Alarm | READ | Supply Damper 3 Feedback Alarm | [0, 1]
SupDmpMB_Siemens2\SupDmpMB_Siemens2.Mechanical_fault | 0=Normal, 1=Alarm | READ | Supply Damper 3 Mechanical Fault | [0, 1]
SupDmpMB_Siemens3\Dmp_Fdb | 0-100% | READ | Supply Damper 4 Feedback | [0, 100]
SupDmpMB_Siemens3\SupDmpMB_Siemens3.CommAlarm | 0=Normal, 1=Alarm | READ | Supply Damper 4 Comm Alarm | [0, 1]
SupDmpMB_Siemens3\SupDmpMB_Siemens3.FeedbackAlarm | 0=Normal, 1=Alarm | READ | Supply Damper 4 Feedback Alarm | [0, 1]
SupDmpMB_Siemens3\SupDmpMB_Siemens3.Mechanical_fault | 0=Normal, 1=Alarm | READ | Supply Damper 4 Mechanical Fault | [0, 1]
FreshDmpMB_Siemens\Dmp_Pos | 0-100% | READ | Fresh Damper Position | [0, 100]
FreshDmpMB_Siemens\Dmp_Fdb | 0-100% | READ | Fresh Damper 1 Feedback | [0, 100]
FreshDmpMB_Siemens\FreshDmpMB_Siemens.CommAlarm | 0=Normal, 1=Alarm | READ | Fresh Damper 1 Comm Alarm | [0, 1]
FreshDmpMB_Siemens\FreshDmpMB_Siemens.FeedbackAlarm | 0=Normal, 1=Alarm | READ | Fresh Damper 1 Feedback Alarm | [0, 1]
FreshDmpMB_Siemens\FreshDmpMB_Siemens.Mechanical_fault | 0=Normal, 1=Alarm | READ | Fresh Damper 1 Mechanical Fault | [0, 1]
FreshDmpMB_Siemens1\Dmp_Fdb | 0-100% | READ | Fresh Damper 2 Feedback | [0, 100]
FreshDmpMB_Siemens1\FreshDmpMB_Siemens1.CommAlarm | 0=Normal, 1=Alarm | READ | Fresh Damper 2 Comm Alarm | [0, 1]
FreshDmpMB_Siemens1\FreshDmpMB_Siemens1.FeedbackAlarm | 0=Normal, 1=Alarm | READ | Fresh Damper 2 Feedback Alarm | [0, 1]
FreshDmpMB_Siemens1\FreshDmpMB_Siemens1.Mechanical_fault | 0=Normal, 1=Alarm | READ | Fresh Damper 2 Mechanical Fault | [0, 1]
FreshDmpMB_Siemens2\Dmp_Fdb | 0-100% | READ | Fresh Damper 3 Feedback | [0, 100]
FreshDmpMB_Siemens2\FreshDmpMB_Siemens2.CommAlarm | 0=Normal, 1=Alarm | READ | Fresh Damper 3 Comm Alarm | [0, 1]
FreshDmpMB_Siemens2\FreshDmpMB_Siemens2.FeedbackAlarm | 0=Normal, 1=Alarm | READ | Fresh Damper 3 Feedback Alarm | [0, 1]
FreshDmpMB_Siemens2\FreshDmpMB_Siemens2.Mechanical_fault | 0=Normal, 1=Alarm | READ | Fresh Damper 3 Mechanical Fault | [0, 1]
FreshDmpMB_Siemens3\Dmp_Fdb | 0-100% | READ | Fresh Damper 4 Feedback | [0, 100]
FreshDmpMB_Siemens3\FreshDmpMB_Siemens3.CommAlarm | 0=Normal, 1=Alarm | READ | Fresh Damper 4 Comm Alarm | [0, 1]
FreshDmpMB_Siemens3\FreshDmpMB_Siemens3.FeedbackAlarm | 0=Normal, 1=Alarm | READ | Fresh Damper 4 Feedback Alarm | [0, 1]
FreshDmpMB_Siemens3\FreshDmpMB_Siemens3.Mechanical_fault | 0=Normal, 1=Alarm | READ | Fresh Damper 4 Mechanical Fault | [0, 1]
ReturnDmpMB_Siemens\Dmp_Pos | 0-100% | READ | Return Damper Position | [0, 100]
ReturnDmpMB_Siemens\Dmp_Fdb | 0-100% | READ | Return Damper 1 Feedback | [0, 100]
ReturnDmpMB_Siemens\ReturnDmpMB_Siemens.CommAlarm | 0=Normal, 1=Alarm | READ | Return Damper 1 Comm Alarm | [0, 1]
ReturnDmpMB_Siemens\ReturnDmpMB_Siemens.FeedbackAlarm | 0=Normal, 1=Alarm | READ | Return Damper 1 Feedback Alarm | [0, 1]
ReturnDmpMB_Siemens\ReturnDmpMB_Siemens.Mechanical_fault | 0=Normal, 1=Alarm | READ | Return Damper 1 Mechanical Fault | [0, 1]
ReturnDmpMB_Siemens1\Dmp_Fdb | 0-100% | READ | Return Damper 2 Feedback | [0, 100]
ReturnDmpMB_Siemens1\ReturnDmpMB_Siemens1.CommAlarm | 0=Normal, 1=Alarm | READ | Return Damper 2 Comm Alarm | [0, 1]
ReturnDmpMB_Siemens1\ReturnDmpMB_Siemens1.FeedbackAlarm | 0=Normal, 1=Alarm | READ | Return Damper 2 Feedback Alarm | [0, 1]
ReturnDmpMB_Siemens1\ReturnDmpMB_Siemens1.Mechanical_fault | 0=Normal, 1=Alarm | READ | Return Damper 2 Mechanical Fault | [0, 1]
ReturnDmpMB_Siemens2\Dmp_Fdb | 0-100% | READ | Return Damper 3 Feedback | [0, 100]
ReturnDmpMB_Siemens2\ReturnDmpMB_Siemens2.CommAlarm | 0=Normal, 1=Alarm | READ | Return Damper 3 Comm Alarm | [0, 1]
ReturnDmpMB_Siemens2\ReturnDmpMB_Siemens2.FeedbackAlarm | 0=Normal, 1=Alarm | READ | Return Damper 3 Feedback Alarm | [0, 1]
ReturnDmpMB_Siemens2\ReturnDmpMB_Siemens2.Mechanical_fault | 0=Normal, 1=Alarm | READ | Return Damper 3 Mechanical Fault | [0, 1]
ReturnDmpMB_Siemens3\Dmp_Fdb | 0-100% | READ | Return Damper 4 Feedback | [0, 100]
ReturnDmpMB_Siemens3\ReturnDmpMB_Siemens3.CommAlarm | 0=Normal, 1=Alarm | READ | Return Damper 4 Comm Alarm | [0, 1]
ReturnDmpMB_Siemens3\ReturnDmpMB_Siemens3.FeedbackAlarm | 0=Normal, 1=Alarm | READ | Return Damper 4 Feedback Alarm | [0, 1]
ReturnDmpMB_Siemens3\ReturnDmpMB_Siemens3.Mechanical_fault | 0=Normal, 1=Alarm | READ | Return Damper 4 Mechanical Fault | [0, 1]
ExtDmpMB_Siemens\Dmp_Pos | 0-100% | READ | Exhaust Damper Position | [0, 100]
ExtDmpMB_Siemens\Dmp_Fdb | 0-100% | READ | Exhaust Damper 1 Feedback | [0, 100]
ExtDmpMB_Siemens\ExtDmpMB_Siemens.CommAlarm | 0=Normal, 1=Alarm | READ | Exhaust Damper 1 Comm Alarm | [0, 1]
ExtDmpMB_Siemens\ExtDmpMB_Siemens.FeedbackAlarm | 0=Normal, 1=Alarm | READ | Exhaust Damper 1 Feedback Alarm | [0, 1]
ExtDmpMB_Siemens\ExtDmpMB_Siemens.Mechanical_fault | 0=Normal, 1=Alarm | READ | Exhaust Damper 1 Mechanical Fault | [0, 1]
ExtDmpMB_Siemens1\Dmp_Fdb | 0-100% | READ | Exhaust Damper 2 Feedback | [0, 100]
ExtDmpMB_Siemens1\ExtDmpMB_Siemens1.CommAlarm | 0=Normal, 1=Alarm | READ | Exhaust Damper 2 Comm Alarm | [0, 1]
ExtDmpMB_Siemens1\ExtDmpMB_Siemens1.FeedbackAlarm | 0=Normal, 1=Alarm | READ | Exhaust Damper 2 Feedback Alarm | [0, 1]
ExtDmpMB_Siemens1\ExtDmpMB_Siemens1.Mechanical_fault | 0=Normal, 1=Alarm | READ | Exhaust Damper 2 Mechanical Fault | [0, 1]
ExtDmpMB_Siemens2\Dmp_Fdb | 0-100% | READ | Exhaust Damper 3 Feedback | [0, 100]
ExtDmpMB_Siemens2\ExtDmpMB_Siemens2.CommAlarm | 0=Normal, 1=Alarm | READ | Exhaust Damper 3 Comm Alarm | [0, 1]
ExtDmpMB_Siemens2\ExtDmpMB_Siemens2.FeedbackAlarm | 0=Normal, 1=Alarm | READ | Exhaust Damper 3 Feedback Alarm | [0, 1]
ExtDmpMB_Siemens2\ExtDmpMB_Siemens2.Mechanical_fault | 0=Normal, 1=Alarm | READ | Exhaust Damper 3 Mechanical Fault | [0, 1]
ExtDmpMB_Siemens3\Dmp_Fdb | 0-100% | READ | Exhaust Damper 4 Feedback | [0, 100]
ExtDmpMB_Siemens3\ExtDmpMB_Siemens3.CommAlarm | 0=Normal, 1=Alarm | READ | Exhaust Damper 4 Comm Alarm | [0, 1]
ExtDmpMB_Siemens3\ExtDmpMB_Siemens3.FeedbackAlarm | 0=Normal, 1=Alarm | READ | Exhaust Damper 4 Feedback Alarm | [0, 1]
ExtDmpMB_Siemens3\ExtDmpMB_Siemens3.Mechanical_fault | 0=Normal, 1=Alarm | READ | Exhaust Damper 4 Mechanical Fault | [0, 1]
DamperCont\DmpAutoManSel_BMS | 0=ManuelStop, 1=Maneul, 2=Auto | WRITE | Damper Auto Manuel Select BMS | [0, 2]
DamperCont\DmpMinRef_BMS | 0-100% | WRITE | Damper Min Referance BMS | [0, 100]
DamperCont\DmpManRef_BMS | 0-100% | WRITE | Damper Manuel Referance BMS | [0, 100]
DamperCont\CO2_Set_BMS | ppm | WRITE | Damper CO2 Set BMS | [0, 2000]
DamperCont\CO2DB_BMS | ppm | WRITE | Damper CO2 Deadband BMS
DamperCont\Dmp_Pid | 0-100% | READ | Damper PID
DamperCont\DmpContTypeSel | 0=Temp + CO2 , 1=CO2 | WRITE | Damper Control Type Select | [0, 1]
MixDmpMB_Siemens\Dmp_Pos | 0-100% | READ | Mix Damper Position | [0, 100]
MixDmpMB_Siemens\Dmp_Fdb | 0-100% | READ | Mix Damper 1 Feedback | [0, 100]
MixDmpMB_Siemens\MixDmpMB_Siemens.CommAlarm | 0=Normal, 1=Alarm | READ | Mix Damper 1 Comm Alarm | [0, 1]
MixDmpMB_Siemens\MixDmpMB_Siemens.FeedbackAlarm | 0=Normal, 1=Alarm | READ | Mix Damper 1 Feedback Alarm | [0, 1]
MixDmpMB_Siemens\MixDmpMB_Siemens.Mechanical_fault | 0=Normal, 1=Alarm | READ | Mix Damper 1 Mechanical Fault | [0, 1]
MixDmpMB_Siemens1\Dmp_Fdb | 0-100% | READ | Mix Damper 2 Feedback | [0, 100]
MixDmpMB_Siemens1\MixDmpMB_Siemens1.CommAlarm | 0=Normal, 1=Alarm | READ | Mix Damper 2 Comm Alarm | [0, 1]
MixDmpMB_Siemens1\MixDmpMB_Siemens1.FeedbackAlarm | 0=Normal, 1=Alarm | READ | Mix Damper 2 Feedback Alarm | [0, 1]
MixDmpMB_Siemens1\MixDmpMB_Siemens1.Mechanical_fault | 0=Normal, 1=Alarm | READ | Mix Damper 2 Mechanical Fault | [0, 1]
MixDmpMB_Siemens2\Dmp_Fdb | 0-100% | READ | Mix Damper 3 Feedback | [0, 100]
MixDmpMB_Siemens2\MixDmpMB_Siemens2.Mechanical_fault | 0=Normal, 1=Alarm | READ | Mix Damper 3 Mechanical Fault | [0, 1]
MixDmpMB_Siemens3\Dmp_Fdb | 0-100% | READ | Mix Damper 4 Feedback | [0, 100]
MixDmpMB_Siemens3\MixDmpMB_Siemens3.Mechanical_fault | 0=Normal, 1=Alarm | READ | Mix Damper 4 Mechanical Fault | [0, 1]
AHUStart\BMS_Mod_en | 0=Local, 1=Bms , 2=Schedule | WRITE | AHU BMS Mod EN | [0, 2]
AHUStart\BMS_Start | 0 = Off, 1= Start | WRITE | AHU BMS Start | [0, 1]
AHUStart\Ahu_Run_Sts | 0 = Off, 1= Run | READ | AHU Run Status | [0, 1]
AHUStart\Local_Start | 0 = Off, 1= Start | WRITE | AHU Local Start | [0, 1]
TmpControl\HV_Fdb_1 | 0-100% | READ | Heating Valve 1 Feedback | [0, 100]
TmpControl\CV_Fdb_1 | 0-100% | READ | Cooling Valve 1 Feedback | [0, 100]
TmpControl\Control_Select_BMS | 0=Supply, 1=Return | WRITE | Temp Control Select BMS | [0, 1]
TmpControl\CV_Pos | 0-100% | READ | Cooling Valve Position | [0, 100]
TmpControl\HV_Pos | 0-100% | READ | Heating Valve Position | [0, 100]
TmpControl\CV_Fdb_2 | 0-100% | READ | Heating Valve 2 Feedback | [0, 100]
TmpControl\HV_Fdb_2 | 0-100% | READ | Cooling Valve 2 Feedback | [0, 100]
TmpControl\Tmp_Set_BMS | 10-80 C | WRITE | Temp Set BMS | [10, 80]
TmpControl\Sup_Min_Tmp_BMS | return mode min supply set | WRITE | Supply Min Temp BMS | [10, 80]
TmpControl\Sup_Max_Tmp_BMS | return mode max supply set | WRITE | Supply Max Temp BMS | [10, 80]
TmpControl\CVModeSel_BMS | 0=Off, 1=Maneul, 2=Auto | WRITE | Cooling Valve Mode Select BMS | [0, 3]
TmpControl\CV_Man_Ref_BMS | 0-100% | WRITE | Cooling Valve Manuel Referance BMS | [0, 100]
TmpControl\HVModeSel_BMS | 0=Off, 1=Maneul, 2=Auto | WRITE | Heating Valve Mode Select BMS | [0, 3]
TmpControl\HV_Man_Ref_BMS | 0-100% | WRITE | Heating Valve Manuel Referance BMS | [0, 100]
TmpControl\Cooling_Active | 0=Off, 1=On | READ | Cooling Mode Active | [0, 1]
TmpControl\Heating_Active | 0=Off, 1=On | READ | Heating Mode Active | [0, 1]
TmpControl\HeatTempSet | C | READ | Heat Calculated Temp Set | [-64, 64]
TmpControl\CoolTempSet | C | READ | Cool Calculated Temp Set | [-64, 64]
MBUnit\BMS_Check_Read |  | READ | BMS Check Read | [0, 1]
MBUnit\BMS_Check_Write |  | WRITE | BMS Check Write | [0, 1]
ElectricalHeater\Heater1_ok | 0=Off, 1=On | READ | Electrical Heater 1 Run | [0, 1]
ElectricalHeater\Heater2_ok | 0=Off, 1=On | READ | Electrical Heater 2 Run | [0, 1]
ElectricalHeater\Heater3_ok | 0=Off, 1=On | READ | Electrical Heater 3 Run | [0, 1]
ElectricalHeater\HeaterStage | 0=Off,1=1.Stage,2=2.Stage,3=3.Stage | READ | Electrical Heater Stage | [0, 3]
ElectricalHeater\HighTempAlarm | 0=Normal, 1=Alarm | READ | Electrical Heater High Temp Alarm | [0, 1]
RotorControl\RotorModeSelBMS | 0=ManuelStop, 1=Maneul, 2=Auto | WRITE | Rotor Mode Select BMS | [0, 2]
RotorControl\RotorManSetBMS | 0-100% | WRITE | Rotor Manuel Set BMS | [0, 100]
RotorControl\RotorMaxSpeed | 0-100% | WRITE | Rotor Max Speed | [0, 100]
RotorControl\RotorPos | 0-100% | READ | Rotor Position | [0, 100]
RotorControl\RotorActive | 0=Off, 1=On | READ | Rotor Active | [0, 1]
RotorControl\Rotor Alarm | 0=Normal, 1=Alarm | READ | Rotor Alarm | [0, 1]
RunAroundCont\RunAraundModeSel1_bms | 0=ManuelStop, 1=Maneul, 2=Auto | WRITE | RunAround Mode Select BMS | [0, 2]
RunAroundCont\RunAr Start | 0=Off, 1=On | READ | RunAround Start | [0, 1]
RunAroundCont\Water_Frost | 0=Normal, 1=Alarm | READ | RunAround Water Frost Alarm | [0, 1]
RunAroundCont\RunAround_Erorr | 0=Normal, 1=Alarm | READ | RunAround Error | [0, 1]
SAF\SAF.ManualReferanceBMS | 0-100% | WRITE | SAF Manuel Referance BMS | [0, 100]
SAF\SAF.ActualManRef | 0-100% | READ | SAF Actual Manuel Referance | [0, 100]
SAF\SAF.ModeSelectBMS | 0=ManuelStop, 1=Maneul, 2=Auto | WRITE | SAF Mode Select BMS | [0, 2]
SAF\SAF.ActualMode | 0=ManuelStop, 1=Maneul, 2=Auto | READ | SAF Actual Mode | [0, 2]
SAF\SAF.AirVolumeSetBMS | m3/h | WRITE | SAF Air Volume Set BMS | [0, 60000]
SAF\SAF.ActualAirVolSet | m3/h | READ | SAF Actual Air Vol Set | [0, 40000]
SAF\SAF.Position | 0-100% | READ | SAF Position | [0, 100]
SAF\SAF.MinimumRef | 0-100% | WRITE | SAF Minimum Referance | [0, 100]
SAF\SAF.Air_FlowFan1 | m3/h | READ | SAF Air Flow Fan 1 | [0, 65536]
SAF\SAF.Air_FlowFan2 | m3/h | READ | SAF Air Flow Fan 2 | [0, 65536]
SAF\SAF.Air_Flow | m3/h | READ | SAF Air Flow | [0, 65536]
SAF\SAF.Start_Delay | s | WRITE | SAF Start Delay | [0, 250]
SAF\SAF.Stop_Delay | s | WRITE | SAF Stop Delay | [0, 250]
SAF\SAF.DelayedStopPos | s | READ | SAF Delayed Stop Position | [0, 100]
SAF\SAF.DelayedStartPos | s | READ | SAF Delayed Start Position | [0, 100]
SAF\SAF.PrHighAlmSet | Pa | WRITE | SAF Pressure High Alarm Set | [0, 10000]
SAF\SAF.DuctPress | Pa | READ | SAF Duct Press | [0, 65536]
SAF\SAF.DuctPressureBMS | Pa | WRITE | SAF Duct Pressure BMS | [0, 7500]
SAF\SAF.InputSelectLocal | 0=m3/h , 1=Pa | WRITE | SAF Input Select Local | [0, 1]
SAF\SAF.ITime | s | WRITE | SAF ITime | [5, 2000]
SAF\SAF.PGain | s | WRITE | SAF PGain | [0.001, 100]
SAF\SAF.ITimePre | s | WRITE | SAF ITimePre | [5, 2000]
SAF\SAF.PGainPre | s | WRITE | SAF PGainPre | [0.001, 100]
SAF\SAF.PrHighAlarm | 0=Normal, 1=Alarm | READ | SAF Pressure High Alarm | [0, 1]
QBM97xx_SAF\QBM97xx_SAF.CommAlarm | 0=Normal, 1=Alarm | READ | SAF Pressure Sensor Comm Alarm | [0, 1]
SAF\SAF.lowAirAlarm | 0=Normal, 1=Alarm | READ | SAF Low Air Flow Alarm | [0, 1]
EAF\EAF.ManualReferanceBMS | 0-100% | WRITE | EAF Manuel Referance BMS | [0, 100]
EAF\EAF.ActualManRef | 0-100% | READ | EAF Actual Manuel Referance | [0, 100]
EAF\EAF.ModeSelectBMS | 0=ManuelStop, 1=Maneul, 2=Auto | WRITE | EAF Mode Select BMS | [0, 2]
EAF\EAF.ActualMode | 0=ManuelStop, 1=Maneul, 2=Auto | READ | EAF Actual Mode | [0, 2]
EAF\EAF.AirVolumeSetBMS | m3/h | WRITE | EAF Air Volume Set BMS | [0, 60000]
EAF\EAF.ActualAirVolSet | m3/h | READ | EAF Actual Air Vol Set | [0, 40000]
EAF\EAF.Position | 0-100% | READ | EAF Position | [0, 100]
EAF\EAF.MinimumRef | 0-100% | WRITE | EAF Minimum Referance | [0, 100]
EAF\EAF.Air_FlowFan1 | m3/h | READ | EAF Air Flow Fan 1 | [0, 65536]
EAF\EAF.Air_FlowFan2 | m3/h | READ | EAF Air Flow Fan 2 | [0, 65536]
EAF\EAF.Air_Flow | m3/h | READ | EAF Air Flow | [0, 65536]
EAF\EAF.Start_Delay | s | WRITE | EAF Start Delay | [0, 250]
EAF\EAF.Stop_Delay | s | WRITE | EAF Stop Delay | [0, 250]
EAF\EAF.DelayedStopPos | s | READ | EAF Delayed Stop Position | [0, 100]
EAF\EAF.DelayedStartPos | s | READ | EAF Delayed Start Position | [0, 100]
EAF\EAF.PrHighAlmSet | Pa | WRITE | EAF Pressure High Alarm Set | [0, 10000]
EAF\EAF.DuctPress | Pa | READ | EAF Duct Press | [0, 65536]
EAF\EAF.DuctPressureBMS | Pa | WRITE | EAF Duct Pressure BMS | [0, 7500]
EAF\EAF.InputSelectLocal | 0=m3/h , 1=Pa | WRITE | EAF Input Select Local | [0, 1]
EAF\EAF.ITime | s | WRITE | EAF ITime | [5, 2000]
EAF\EAF.PGain | s | WRITE | EAF PGain | [0.001, 100]
EAF\EAF.ITimePre | s | WRITE | EAF ITimePre | [5, 2000]
EAF\EAF.PGainPre | s | WRITE | EAF PGainPre | [0.001, 100]
EAF\EAF.PrHighAlarm | 0=Normal, 1=Alarm | READ | EAF Pressure High Alarm | [0, 1]
QBM97xx_EAF\QBM97xx_EAF.CommAlarm | 0=Normal, 1=Alarm | READ | EAF Pressure Sensor Comm Alarm | [0, 1]
EAF\EAF.lowAirAlarm | 0=Normal, 1=Alarm | READ | EAF Low Air Flow Alarm | [0, 1]
HumModeSel1\HumModeSel1.Start | 0=Stopped, 1=Running | READ | Humidifier 1 Start | [0, 1]
Hum_Mod_Sel\Hum_RunSts1 | 0=Stopped, 1=Running | READ | Humidifier 1 Run Status | [0, 1]
HumModeSel1\HumModeSel1.ManPosBMS | 0-100% | WRITE | Humidifier 1 Manuel Position BMS | [0, 100]
HumModeSel1\HumModeSel1.ModeSelBMS | 0=ManuelStop, 1=Maneul, 2=Auto | WRITE | Humidifier 1 Mode Select BMS | [0, 2]
Hum_Mod_Sel\Hum_Alarm1 | 0=Normal, 1=Alarm | READ | Humidifier Alarm 1 | [0, 1]
HumModeSel2\HumModeSel2.Start | 0=Stopped, 1=Running | READ | Humidifier 2 Start | [0, 1]
Hum_Mod_Sel\Hum_RunSts2 | 0=Stopped, 1=Running | READ | Humidifier 2 Run Status | [0, 1]
HumModeSel2\HumModeSel2.ManPosBMS | 0-100% | WRITE | Humidifier 2 Manuel Position BMS | [0, 100]
HumModeSel2\HumModeSel2.ModeSelBMS | 0=ManuelStop, 1=Maneul, 2=Auto | WRITE | Humidifier 2 Mode Select BMS | [0, 2]
Hum_Mod_Sel\Hum_Alarm2 | 0=Normal, 1=Alarm | READ | Humidifier Alarm 2 | [0, 1]
HumModeSel3\HumModeSel3.Start | 0=Stopped, 1=Running | READ | Humidifier 3 Start | [0, 1]
Hum_Mod_Sel\Hum_RunSts3 | 0=Stopped, 1=Running | READ | Humidifier 3 Run Status | [0, 1]
HumModeSel3\HumModeSel3.ManPosBMS | 0-100% | WRITE | Humidifier 3 Manuel Position BMS | [0, 100]
HumModeSel3\HumModeSel3.ModeSelBMS | 0=ManuelStop, 1=Maneul, 2=Auto | WRITE | Humidifier 3 Mode Select BMS | [0, 2]
Hum_Mod_Sel\Hum_Alarm3 | 0=Normal, 1=Alarm | READ | Humidifier Alarm 3 | [0, 1]
HumModeSel4\HumModeSel4.Start | 0=Stopped, 1=Running | READ | Humidifier 4 Start | [0, 1]
Hum_Mod_Sel\Hum_RunSts4 | 0=Stopped, 1=Running | READ | Humidifier 4 Run Status | [0, 1]
HumModeSel4\HumModeSel4.ManPosBMS | 0-100% | WRITE | Humidifier 4 Manuel Position BMS | [0, 100]
HumModeSel4\HumModeSel4.ModeSelBMS | 0=ManuelStop, 1=Maneul, 2=Auto | WRITE | Humidifier 4 Mode Select BMS | [0, 2]
Hum_Mod_Sel\Hum_Alarm4 | 0=Normal, 1=Alarm | READ | Humidifier Alarm 4 | [0, 1]
HumModeSel5\HumModeSel5.Start | 0=Stopped, 1=Running | READ | Humidifier 5 Start | [0, 1]
Hum_Mod_Sel\Hum_RunSts5 | 0=Stopped, 1=Running | READ | Humidifier 5 Run Status | [0, 1]
HumModeSel5\HumModeSel5.ManPosBMS | 0-100% | WRITE | Humidifier 5 Manuel Position BMS | [0, 100]
HumModeSel5\HumModeSel5.ModeSelBMS | 0=ManuelStop, 1=Maneul, 2=Auto | WRITE | Humidifier 5 Mode Select BMS | [0, 2]
Hum_Mod_Sel\Hum_Alarm5 | 0=Normal, 1=Alarm | READ | Humidifier Alarm 5 | [0, 1]
HumModeSel6\HumModeSel6.Start | 0=Stopped, 1=Running | READ | Humidifier 6 Start | [0, 1]
Hum_Mod_Sel\Hum_RunSts6 | 0=Stopped, 1=Running | READ | Humidifier 6 Run Status | [0, 1]
HumModeSel6\HumModeSel6.ManPosBMS | 0-100% | WRITE | Humidifier 6 Manuel Position BMS | [0, 100]
HumModeSel6\HumModeSel6.ModeSelBMS | 0=ManuelStop, 1=Maneul, 2=Auto | WRITE | Humidifier 6 Mode Select BMS | [0, 2]
Hum_Mod_Sel\Hum_Alarm6 | 0=Normal, 1=Alarm | READ | Humidifier Alarm 6 | [0, 1]
HumModeSel7\HumModeSel7.Start | 0=Stopped, 1=Running | READ | Humidifier 7 Start | [0, 1]
Hum_Mod_Sel\Hum_RunSts7 | 0=Stopped, 1=Running | READ | Humidifier 7 Run Status | [0, 1]
HumModeSel7\HumModeSel7.ManPosBMS | 0-100% | WRITE | Humidifier 7 Manuel Position BMS | [0, 100]
HumModeSel7\HumModeSel7.ModeSelBMS | 0=ManuelStop, 1=Maneul, 2=Auto | WRITE | Humidifier 7 Mode Select BMS | [0, 2]
Hum_Mod_Sel\Hum_Alarm7 | 0=Normal, 1=Alarm | READ | Humidifier Alarm 7 | [0, 1]
HumModeSel8\HumModeSel8.Start | 0=Stopped, 1=Running | READ | Humidifier 8 Start | [0, 1]
Hum_Mod_Sel\Hum_RunSts8 | 0=Stopped, 1=Running | READ | Humidifier 8 Run Status | [0, 1]
HumModeSel8\HumModeSel8.ManPosBMS | 0-100% | WRITE | Humidifier 8 Manuel Position BMS | [0, 100]
HumModeSel8\HumModeSel8.ModeSelBMS | 0=ManuelStop, 1=Maneul, 2=Auto | WRITE | Humidifier 8 Mode Select BMS | [0, 2]
Hum_Mod_Sel\Hum_Alarm8 | 0=Normal, 1=Alarm | READ | Humidifier Alarm 8 | [0, 1]
Hum_Mod_Sel\NumberOf_Hum | 0-8 | WRITE | Humidifier Capacity | [0, 8]
Hum_Mod_Sel\SaturTemp | C | READ | Humidifier Saturated Temp | [-64, 64]
Hum_Mod_Sel\CalHumSet | g/kg | READ | Humidifier Calculated Hum Set | [-64, 64]
Hum_Mod_Sel\HUM_Set_bms | 0-100% | WRITE | Hum Set BMS | [4, 20]
Hum_Mod_Sel\Sup_HUM_Max_bms | 0-100% | WRITE | Supply Hum Max BMS | [4, 20]
Hum_Mod_Sel\Sup_HUM_Min_bms | 0-100% | WRITE | Supply Hum Min BMS | [4, 20]
Hum_Mod_Sel\DB_HUM_SET_bms | 0-5 | WRITE | Deadband Hum Set BMS | [0, 5]
Hum_Mod_Sel\HUMContTypeSel_bms | 0=Supply, 1=Return | WRITE | Hum Control Type Select BMS | [0, 1]
Hum_Mod_Sel\Humectation ON | 0=Off, 1=On | READ | Humectation ON | [0, 1]
Hum_Mod_Sel\DeHumectation on | 0=Off, 1=On | READ | Dehumectation ON | [0, 1]
Hum_Mod_Sel\HumSet_Abs | g/kg | READ | Hum Set ABS | [-64, 64]
Hum_Mod_Sel\Room_Abs | g/kg | READ | Humidifier Room ABS | [-64, 64]
Hum_Mod_Sel\RoomHumSel | 0=Off, 1=On | WRITE | Humidifier Room Hum Sel | [0, 1]
WetBulp_Temp | C | READ | Humidifier WetBulp Temp | [-64, 64]
TmpControl\COControl_Select | 0=Off, 1=Auto, 2=Heat, 3=Cool | WRITE | ChangeOver Valve Control Select | [0, 3]
TmpControl\CoverVModeSel | 0=Off, 1=Manuel, 2=Auto | WRITE | ChangeOver Valve Mode Sel | [0, 2]
TmpControl\CoverMan_Ref | 0-100% | WRITE | ChangeOver Valve Manuel Referance | [0, 100]
TmpControl\COContTempValue | C | WRITE | ChangeOver Valve Control Temp Value | [-64, 64]
TmpControl\ChangeOvFdb | 0-100% | READ | ChangeOver Valve Feedback | [0, 100]
TmpControl\ChangeOvPos | 0-100% | READ | ChangeOver Valve Position | [0, 100]
TmpControl\COControl_Select_BMS | 0=Off, 1=Auto, 2=Heat, 3=Cool | WRITE | ChangeOver Valve Control Select BMS | [0, 3]
TmpControl\CoverVModeSel_BMS | 0=Off, 1=Manuel, 2=Auto | WRITE | ChangeOver Valve Mode Select BMS | [0, 2]
TmpControl\CoverMan_Ref_BMS | 0-100% | WRITE | ChangeOver Valve Manuel Referance BMS | [0, 100]
TmpControl\ChangeOverActive | 0=Off, 1=On | READ | ChangeOver Valve Active | [0, 1]
TmpControl\ChangeOverMode | 0=Off, 1=Heat, 2=Cool | READ | ChangeOver Valve Mode | [0, 2]